## DataBase
FISCAL YEAR 2020-2021
|  | 31 | 31 | 30 | 31 | 30 | 31 | 31 | 28 | 31 | 30 | 31 | 0
|  | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY | JUN | FYTD | FYTD-AVG
Item | Index | 7 | 8 | 9 | 10 | 12 | 12 | 13 | 14 | 15 | 16 | 17 | 18
Total System Generation |  | 25719.9895 | 25797.0635 | 24243.5125 | 24404.586 | 22938.64 | 22207.3064 | 21720.8868 | 19883.8923 | 22354.9132 | 21899.6515 | 24293.7255 |  | 255464.1672 | 23224.0152
Gross Power Generation |  | 25075.95 | 25132.08 | 23591.11 | 23735.79 | 22338.04 | 21615.68 | 21130.86 | 19245.18 | 21627.69 | 21204.86 | 23621.77 |  | 248319.01 | 22574.4555
Gross Water Production |  | 90987.3333 | 89121.8333 | 82706.1667 | 88049.8333 | 87245.3333 | 88737.3333 | 98485.5 | 87791.8333 | 102458.6667 | 96396.3333 | 104287.8333 |  | 1016268 | 92388
System Load Factor |  | 82.05% | 80.83% | 81.77% | 81.1% | 78.74% | 77.83% | 74.31% | 80.67% | 78.99% | 78.79% | 82.57% |  | 877.7% | 79.79%
Total No. 6 Fuel Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Total No. 2 Fuel Cost |  | 426605.2954 | 639765.748 | 1161061.1421 | 134059.983 | 151618.4179 | 142478.9617 | 287462.368 | 111350.8443 | 163190.9234 | 1323140.361 | 166608.3951 |  | 4707342.4398 | 427940.2218
Total Propane Cost |  | 3453706.8756 | 3267490.988 | 2553332.1795 | 3331088.4222 | 3278983.919 | 3530353.84 | 4147376.4276 | 3759547.2414 | 4409679.0073 | 2936217.3309 | 4303842.95 |  | 38971619.1815 | 3542874.471
Power Fuel Cost (Internal) |  | 0.15474 | 0.15547 | 0.15745 | 0.14599 | 0.15358 | 0.16992 | 0.20987 | 0.20114 | 0.21144 | 0.20087 | 0.18925 |  | 1.9497 | 0.17725
Power Fuel Cost (to bus) |  | 0.16018 | 0.16268 | 0.16406 | 0.15209 | 0.16122 | 0.17624 | 0.22441 | 0.21123 | 0.22162 | 0.19889 | 0.20494 |  | 2.0376 | 0.18523
Water Fuel Cost (Internal) |  | 1.8354 | 1.8234 | 1.8371 | 1.6996 | 1.7806 | 1.9862 | 2.4964 | 2.3764 | 2.5432 | 2.4057 | 2.2524 |  | 23.0365 | 2.0942
Water Fuel Cost (to Distribution |  | 1.872 | 1.8621 | 1.8651 | 1.7235 | 1.812 | 2.0222 | 2.5423 | 2.4197 | 2.5888 | 2.456 | 2.2882 |  | 23.4519 | 2.132
Total Power Fuel Cost |  | 3713314.5045 | 3744752.5614 | 3562453.9143 | 3315497.8093 | 3275251.6783 | 3496583.1529 | 4188975.5048 | 3662267.9831 | 4312300.3544 | 4027455.6774 | 4235553.1644 |  | 41534406.3047 | 3775855.1186
Total Water Fuel Cost |  | 166997.6665 | 162504.1747 | 151939.4073 | 149650.5959 | 155350.6585 | 176249.6488 | 245863.2908 | 208630.1026 | 260569.5762 | 231902.0145 | 234898.1807 |  | 2144555.3166 | 194959.5742
No. 6 Fuel Consumed |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
No. 2 Fuel Consumed |  | 5520.1249 | 9234.3241 | 16758.6572 | 1935.0103 | 2188.4473 | 2056.614 | 4149.3782 | 1607.2953 | 2355.5808 | 18615.4767 | 2344.0406 |  | 66764.9496 | 6069.5409
No. 6 Fuel Received |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
No. 2 Fuel Received |  | 0 | 32182.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12057.52 | 0 |  | 44239.64 | 22119.82
EOM No. 6 Fuel On Hand |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
EOM No. 2 Fuel On Hand(based on 2000Bbl/day Consumption) |  | 17.1102 | 28.5841 | 20.2048 | 19.2373 | 18.1431 | 17.1148 | 15.0401 | 14.2364 | 13.0586 | 9.7796 | 8.6076 |  | 181.1166 | 16.4651
Plant Water Use ( Internal) |  | 15419.311 | 1905.8303 | 2090.0527 | 1555.6764 | 1504.9232 | 1581.128 | 2214.499 | 1406.5682 | 1881.5781 | 2463.5082 | 1896.7362 |  | 33919.8114 | 3083.6192
Plant Power Use (Internal) |  | 205429.6386 | 202269.0761 | 191866.8631 | 185910.594 | 190442.1069 | 220693.5206 | 312429.1532 | 277296.7445 | 341482.2609 | 308113.4825 | 297088.0142 |  | 2733021.4547 | 248456.4959
Heat Rates BTU/KWH | [13 empty] | 0 | 0
(Net Energy in KWH Produced) | [13 empty] | 0 | 0
Units | [13 empty] | 0 | 0
Combined Cycle-Units 10,16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Combined Cycle-Units 11,16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 10-Steam (10 MW) |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | 0 | 0
Unit 11-Steam (21 MW) |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | 0 | 0
Unit 16-Gas Turbine (23 MW) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 17-Gas Turbine (20.3 MW) |  | 19723.3655 | 19377.4218 | 19918.1643 | 20433.9315 | 20902.8681 | 21861.1136 | 20842.1156 | 18459.5883 | 17358.7518 | 17834.7827 | 16711.7077 |  | 213423.8109 | 19402.1646
Unit 19-Gas Turbine (24 MW) |  | 31163.4711 | 25705.1735 | 19292.4251 | 22369.8317 | 21548.3601 | 24977.4508 | 21940.2019 | 18210.4459 | 0 | 18663.5897 | 19871.9642 |  | 223742.914 | 22374.2914
Unit 20_Gas Turbine (24 MW) |  | 0 | 0 | 0 | 0 | 0 | 41467.1816 | 20598.0852 | 21478.4125 | 21492.3551 | 19161.0459 | 22417.5719 |  | 146614.6521 | 24435.7754
Aggreko |  | 10887.2856 | 10962.7384 | 10998.875 | 10904.2078 | 10898.0236 | 10911.9193 | 11041.1381 | 11140.594 | 11389.2762 | 11151.2222 | 11025.5448 |  | 121310.8251 | 11028.2568
Total Plant . |  | 15100.2454 | 15206.0874 | 15197.1983 | 14624.6701 | 14782.9218 | 15044.4226 | 15397.26 | 14863.9622 | 14844.2832 | 15523.0581 | 14339.8289 |  | 164923.9381 | 14993.0853
Desal Performance Ratios | [13 empty] | 0 | 0
IDE3 (1.25MGD) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE4 (.55MGD) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE5 (0.55MGD) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE9 (1.3MGD) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit Availability Percent | [13 empty] | 0 | 0
Unit 10 | [13 empty] | 0% | 0% | bar: 7 to 17
Unit 11 | [13 empty] | 0% | 0% | bar: 7 to 17
Unit 16 | [13 empty] | 0% | 0% | bar: 7 to 17
Unit 17 |  | 100% | 100% | 96.3% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 1096% | 99.66%
Unit 19 |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 1100% | 100%
Unit 20 |  | 0% | 0% | 0% | 0% | 0% | 2.78% | 100% | 100% | 100% | 100% | 100% |  | 502.8% | 45.71%
Aggreko |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 1100% | 100%
IDE 3 |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 1100% | 100%
IDE 4 | [13 empty] | 0% | 0% | bar: 7 to 17
IDE 5 | [13 empty] | 0% | 0% | bar: 7 to 17
IDE 9 |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 1100% | 100%
HRSG 21 | [13 empty] | 0% | 0% | bar: 7 to 17
HRSG 24 |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 1100% | 100%
Pag2 | [13 empty] | 0 | 0
Item | [13 empty] | 0 | 0
Steam Turbine Generation |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Gas Turbine Generation |  | 25075950 | 25132080 | 23591110 | 23735790 | 22338040 | 21615680 | 21130860 | 19245180 | 21627690 | 21204860 | 23621770 |  | 248319010 | 22574455.4545
Diesel Generation |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Total Generation |  | 25075950 | 25132080 | 23591110 | 23735790 | 22338040 | 21615680 | 21130860 | 19245180 | 21627690 | 21204860 | 23621770 |  | 248319010 | 22574455.4545
IPP1 |  | 644039.5 | 664983.5 | 652402.5 | 668796 | 600600 | 591626.406 | 590026.844 | 638712.25 | 727223.25 | 694791.5 | 671955.5 |  | 7145157.25 | 649559.75
Total System Generation |  | 25719989.5 | 25797063.5 | 24243512.5 | 24404586 | 22938640 | 22207306.406 | 21720886.844 | 19883892.25 | 22354913.25 | 21899651.5 | 24293725.5
Steam Station Power |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Gas Turbine Station Power |  | 45390 | 45350 | 49610 | 36910 | 35210 | 62750 | 103800 | 115400 | 110730 | 131040 | 97330 |  | 833520 | 75774.5455
Total Gen. Plant Station Power |  | 45390 | 45350 | 49610 | 36910 | 35210 | 62750 | 103800 | 115400 | 110730 | 131040 | 97330 |  | 833520 | 75774.5455
Total Service / Gross Output |  | 0.181% | 0.1804% | 0.2103% | 0.1555% | 0.1576% | 0.2903% | 0.4912% | 0.5996% | 0.512% | 0.618% | 0.412% |  | 3.808% | 0.3462%
Operating Hours | [13 empty] | 0 | 0
Unit 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 11 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 17 |  | 739.5 | 722.8 | 610.5 | 728.2 | 704.3 | 727.4 | 414.1 | 80.2 | 282.6 | 136 | 404.8 |  | 5550.4 | 504.5818
Unit 19 |  | 180.1 | 242.4 | 287.9 | 41.9 | 58.7 | 29.4 | 86.3 | 29 | 0.8 | 83.9 | 53.6 |  | 1094 | 99.4545
Unit 20 |  | 0 | 0 | 0 | 0 | 0 | 19.6 | 401.3 | 592.8 | 489.6 | 720.3 | 314.2 |  | 2537.8 | 422.9667
Aggreko |  | 713.003 | 697.0245 | 639.6298 | 741.0772 | 691.7374 | 728.6257 | 0 | 607.523 | 649.509 | 620.7836 | 0 |  | 6088.9132 | 676.5459
Diesel Generation(Emergency) |  | 1 | 3 | 0 | 3 | 1 | 1 | 1 | 2 | 1 | 1 | 2 |  | 16 | 1.6
Unit Average Loading | [13 empty] | 0 | 0
(KWH / Operating Hours) | [13 empty] | 0 | 0
Unit 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 11 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 17 |  | 13623.1508 | 13655.7831 | 13025.7166 | 12180.1154 | 11559.9035 | 10267.5282 | 10396.6192 | 10720.6983 | 11102.3355 | 14425.8824 | 12980.9289 |  | 133938.6615 | 12176.242
Unit 19 |  | 4553.0261 | 6600.6601 | 11774.9218 | 7875.895 | 8517.8876 | 7142.8571 | 7995.365 | 10000 | 0 | 13230.0358 | 9888.0597 |  | 87578.7082 | 8757.8708
Unit 20 |  | 0 | 0 | 0 | 0 | 0 | 7677.551 | 11037.9267 | 10331.444 | 11313.2353 | 12349.9653 | 12214.895 |  | 64925.0173 | 10820.8362
Aggreko |  | 19890 | 19600 | 19150 | 19615 | 19800 | 18921.375 | 0 | 19704.4402 | 19940 | 14880 | 0 |  | 171500.8152 | 19055.6461
Diesel |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Utilization Factor | [13 empty] | 0 | 0
Unit 10 | [13 empty] | 0% | 0% | bar: 7 to 17
Unit 11 | [13 empty] | 0% | 0% | bar: 7 to 17
Unit 16 | [13 empty] | 0% | 0% | bar: 7 to 17
Unit 17 |  | 62.21% | 62.36% | 59.48% | 55.62% | 52.78% | 46.88% | 47.47% | 48.95% | 50.7% | 65.87% | 59.27% |  | 611.6% | 55.6%
Unit 19 |  | 18.58% | 26.94% | 48.06% | 32.15% | 34.77% | 29.15% | 32.63% | 40.82% | 0% | 54% | 40.36% |  | 357.5% | 35.75%
Unit 20 |  | 0% | 0% | 0% | 0% | 0% | 31.34% | 45.05% | 42.17% | 46.18% | 50.41% | 49.86% |  | 265% | 44.17%
Aggreko |  | 99.45% | 98% | 95.75% | 98.08% | 99% | 94.61% | 0% | 98.52% | 99.7% | 74.4% | 0%
Diesel | 1 | [12 empty] | 0% | 0% | bar: 7 to 17
Unit Output KW | 2 | [12 empty] | 0 | 0
Unit 10 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 11 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 17 | 6 | 10074320 | 9870400 | 7952200 | 8869560 | 8141640 | 7468600 | 4305240 | 859800 | 3137520 | 1961920 | 5254680 |  | 67895880 | 6172352.7273
Unit 19 | 7 | 820000 | 1600000 | 3390000 | 330000 | 500000 | 210000 | 690000 | 290000 | 0 | 1110000 | 530000 |  | 9470000 | 947000
Unit 20 | 8 | 0 | 0 | 0 | 0 | 0 | 150480 | 4429520 | 6124480 | 5538960 | 8895680 | 3837920 |  | 28977040 | 4829506.6667
Aggreko |  | 14181630 | 13661680 | 12248910 | 14536230 | 13696400 | 13786600 | 11706100 | 11970900 | 12951210 | 9237260 | 13999170 |  | 141976090 | 12906917.2727
Diesel |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TOTAL | 9 | 25075950 | 25132080 | 23591110 | 23735790 | 22338040 | 21615680 | 21130860 | 19245180 | 21627690 | 21204860 | 23621770 |  | 248319010 | 22574455.4545
Unit Station Service Power | [13 empty] | 0 | 0
Unit 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 11 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 17 |  | 2370 | 3560 | 6150 | 2820 | 2490 | 2640 | 14000 | 23790 | 19220 | 21700 | 12300 |  | 111040 | 10094.5455
Unit 19 |  | 35520 | 34800 | 36960 | 27680 | 27120 | 27440 | 28160 | 22800 | 26880 | 27680 | 28000 |  | 323040 | 29367.2727
Unit 20 |  | 7500 | 6990 | 6500 | 6410 | 5600 | 32670 | 61640 | 68810 | 64630 | 81660 | 57030 |  | 399440 | 36312.7273
Aggreko |  | 260 | 450 | 2350 | 670 | 230 | 400 | 470 | 790 | 3300 | 11820 | 410 |  | 21150 | 1922.7273
Diesel |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TOTAL |  | 45390 | 45350 | 49610 | 36910 | 35210 | 63150 | 104270 | 116190 | 114030 | 142860 | 97740 |  | 850710 | 77337.2727
pag3 | [13 empty] | 0 | 0
BOILERS/STM. TURBINES | [13 empty] | 0 | 0
[14 empty] | 0 | 0
SS10 Plant Aux. Trans 480V |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
SS10 Unit Aux.. Trans 480V |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
[14 empty] | 0 | 0
Unit 10 Total Station Power |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
SS11 Plant Aux. Trans 480V |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
SS11 Unit Aux.. Trans 480V |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
[14 empty] | 0 | 0
Unit 11 Net Total Station Power |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
HRSG 21 Station Power |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HRSG 24 Station Power |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
WHB Net Station Power |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
TOTAL BOILERS / STM TURBINES |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
GAS TURBINE | [13 empty] | 0 | 0
[14 empty] | 0 | 0
Plant SS | [13 empty] | 0 | 0
Unit 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 17 |  | 30 | 980 | 4410 | 780 | 690 | 600 | 12920 | 23610 | 18380 | 21400 | 11400 |  | 95200 | 8654.5455
Unit 19 |  | 35520 | 34800 | 36960 | 27680 | 27120 | 27440 | 28160 | 22800 | 26880 | 27680 | 28000 |  | 323040 | 29367.2727
Unit 20 |  | 0 | 5490 | 6500 | 6410 | 5600 | 32670 | 61640 | 68810 | 64630 | 81660 | 57030 |  | 390440 | 39044
|  | 260 | 450 | 2350 | 670 | 230 | 400 | 470 | 790 | 3300 | 11820 | 410 |  | 21150 | 1922.7273
Unit SS | [13 empty] | 0 | 0
Unit 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 17 |  | 2340 | 2580 | 1740 | 2040 | 1800 | 2040 | 1080 | 180 | 840 | 300 | 900 |  | 15840 | 1440
Unit 19 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 20 |  | 7500 | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9000 | 4500
|  | 9840 | 4080 | 1740 | 2040 | 1800 | 2040 | 1080 | 180 | 840 | 300 | 900 |  | 24840 | 2258.1818
Plant IDE pumpage | [13 empty] | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
[14 empty] | 0 | 0
Total |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
TOTAL GAS TURBINES |  | 45650 | 45800 | 51960 | 37580 | 35440 | 63150 | 104270 | 116190 | 114030 | 142860 | 97740 |  | 854670 | 77697.2727
STX. EMERGENCY DIESEL | [13 empty] | 0 | 0
[14 empty] | 0 | 0
Diesel |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
TOTAL DIESEL |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
WATER PLANTS | [13 empty] | 0 | 0
[14 empty] | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Intake Pump A |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Intake Pump B |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Intake Pump C |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE Intake Pumps A&B+Chloropac |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
RO Plant |  | 458594 | 477312 | 395292 | 448162 | 427195 | 459956 | 515267 | 427483 | 542549 | 477773 | 533093 |  | 5162676 | 469334.1818
UPW Electricity |  | 17911 | 17174 | 15510 | 15316 | 14254.62 | 14855 | 15579.12 | 13681.13 | 16451.88 | 14201.49 | 13209.76 |  | 168144 | 15285.8182
RO ANNEX Electricity |  | 620604 | 567940 | 569716 | 576924 | 584356 | 577324 | 656208 | 609776 | 689832 | 676732 | 708104 |  | 6837516 | 621592.3636
TOTAL WATER PLANTS |  | 1097109 | 1062426 | 980518 | 1040402 | 1025805.62 | 1052135 | 1187054.12 | 1050940.13 | 1248832.88 | 1168706.49 | 1254406.76 |  | 12168336 | 1106212.3636
OTHERS | [13 empty] | 0 | 0
[14 empty] | 0 | 0
Station Service Shops |  | 25440 | 31680 | 29640 | 27480 | 26160 | 25800 | 25320 | 26640 | 28680 | 11280 | 0 |  | 258120 | 25812
Station Service Office | [13 empty] | 0 | 0
Fuel Tanks SS | [13 empty] | 0 | 0
Switch Yard SS |  | 159360 | 161120 | 156480 | 168000 | 152640 | 157760 | 172000 | 166240 | 203040 | 190080 | 195200 |  | 1881920 | 171083.6364
|  | 14: 591; 15: 690; 16: 655; 17: 700 | 2636 | 659
|  | 14: 18052; 15: 19790; 16: 20336; 17: 21760 | 79938 | 19984.5
TOTAL OTHERS |  | 184800 | 192800 | 186120 | 195480 | 178800 | 183560 | 197320 | 211523 | 252200 | 222351 | 217660 |  | 2222614 | 202055.8182
|  | 17: 65041 | 65041 | 65041
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
SwitchGear Bkr1 SS |  | 1126712.5 | 1097708.5 | 1046123 | 1076282.5 | 1059253 | 1087062.87 | 1218442.13 | 1079256.5 | 1280661.5 | 1246724 | 1291947 |  | 12610173.5 | 1146379.4091
SwitchGear Bkr3 SS |  | 301288.25 | 306636 | 302425.25 | 302817.5 | 284381.05 | 317414.7 | 369246.25 | 361867 | 402011.75 | 408122.5 | 382096 |  | 3738306.25 | 339846.0227
[14 empty] | 0 | 0
Total |  | 1428000.75 | 1404344.5 | 1348548.25 | 1379100 | 1343634.05 | 1404477.57 | 1587688.38 | 1441123.5 | 1682673.25 | 1654846.5 | 1674043 |  | 16348479.75 | 1486225.4318
Total SS from GAC |  | 9840 | 4080 | 1740 | 2040 | 1800 | 2040 | 1080 | 180 | 840 | 300 | 900 |  | 24840 | 2258.1818
Total Station Service Power |  | 1327559 | 1301026 | 1218598 | 1273462 | 1240045.62 | 1298845 | 1488644.12 | 1378653.13 | 1615062.88 | 1533917.49 | 1569806.76 |  | 15245620 | 1385965.4545
Total Unit #11 SS (Not Plant) | [13 empty] | 0 | 0
Total Unit #10 SS (Not Plant) | [13 empty] | 0 | 0
[14 empty] | 0 | 0
TOTAL STATION POWER |  | 1327559 | 1301026 | 1218598 | 1273462 | 1240045.62 | 1298845 | 1488644.12 | 1378653.13 | 1615062.88 | 1533917.49 | 1569806.76 |  | 15245620 | 1385965.4545
KWH | [13 empty] | 0
ENERGY DISTRIBUTION | [13 empty] | 0
0
0
0
0
GROSS ENERGY DISTRIBUTION | [13 empty] | 0
Gross Electric Energy Produced |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Gross Energy Used in Water Plants |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
PLANT TOTAL GROSS ENERGY USED |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
0
NET ENERGY DISTRIBUTION | [13 empty] | 0
Net Electricity to Distribution |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Net Energy used on water to distribution |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
PLANT TOTAL NET ENERGY USED |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
0
Plant Service / Gross Output |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
0
BTU's | [13 empty] | 0
Fuel No. 2 Consumed (BTU's) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Fuel No. 6 Consumed (BTU's) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
TOTAL ENERGY IN FUEL |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
0
GROSS ENERGY DISTRIBUTION | [13 empty] | 0
Gross Electric Energy Produced |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Gross Energy Used in Water Plants |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
PLANT TOTAL GROSS ENERGY USED |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
0
NET ENERGY DISTRIBUTION | [13 empty] | 0
Net Electricity to Distribution |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Net Energy used on water to distribution |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
PLANT TOTAL NET ENERGY USED |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
0
Plant Service / NET Output |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
0
EFFICIENCY | [13 empty] | 0
0
Gross Efficiency | [13 empty] | 0
Electric Generating Plant Only |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Water Desalination Plant only |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Combined Generating and Water Plant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
0
Net Efficiency | [13 empty] | 0
Electric Generating Plant Only |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Water Desalination Plant only |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Combined Generating and Water Plant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
0
Heat Rates BTU/KWH | [13 empty] | 0
0
Gross Heat Rate | [13 empty] | 0
Electric Generating Plant Only |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Water Desalination Plant only |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Combined Generating and Water Plant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
0
Net Heat Rate | [13 empty] | 0
Electric Generating Plant Only |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Water Desalination Plant only |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Combined Generating and Water Plant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[14 empty] | 0 | 0
pag4 | [13 empty] | 0 | 0
Desalination Plants Summary | [13 empty] | 0 | 0
Unit Service HRS | [13 empty] | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit Output GALS | [13 empty] | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
From TC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
RO WAPA Meter |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
RO 7Seas water Meter 1 |  | 37516000 | 39683000 | 32676000 | 37374000 | 36186000 | 38640000 | 42643000 | 35802000 | 44494000 | 39665000 | 44312000 |  | 428991000 | 38999181.8182
RO 7Seas water Meter 2 |  | 37390000 | 39542000 | 32563000 | 37249000 | 36082000 | 38582000 | 42548000 | 35729000 | 44482000 | 39709000 | 44207000 |  | 428083000 | 38916636.3636
RO Meter Average |  | 37453000 | 39612500 | 32619500 | 37311500 | 36134000 | 38611000 | 42595500 | 35765500 | 44488000 | 39687000 | 44259500 |  | 428537000 | 38957909.0909
RO 7Seas ANNEXwater Meter 1 |  | 53489000 | 49507000 | 50040000 | 50630000 | 51000000 | 50089000 | 55786000 | 51969000 | 57681000 | 56621000 | 60110000
RO 7Seas ANNEX water Meter 2 |  | 53630000 | 49527000 | 50154000 | 50942000 | 51229000 | 50195000 | 56097000 | 52176000 | 58370000 | 56845000 | 60030000
RO 7Seas ANNEX water Meter 3 |  | 53484000 | 49494000 | 50066000 | 50643000 | 51105000 | 50095000 | 55787000 | 51934000 | 57861000 | 56662000 | 59945000
RO Meter Average |  | 53534333.3333 | 49509333.3333 | 50086666.6667 | 50738333.3333 | 51111333.3333 | 50126333.3333 | 55890000 | 52026333.3333 | 57970666.6667 | 56709333.3333 | 60028333.3333 |  | 587731000 | 53430090.9091
STX TOTALS |  | 90987333.3333 | 89121833.3333 | 82706166.6667 | 88049833.3333 | 87245333.3333 | 88737333.3333 | 98485500 | 87791833.3333 | 102458666.6667 | 96396333.3333 | 104287833.3333 |  | 1016268000 | 92388000
Unit Cond LBS | [13 empty] | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
STX TOTALS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit LP Steam LBS | [13 empty] | 0 | 0
[14 empty] | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
STX TOTALS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit HP Steam LBS | [13 empty] | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
STT TOTALS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit Utilization Factor Percent | [13 empty] | 0% | 0%
IDE 3 | [13 empty] | 0% | 0% | bar: 7 to 17
IDE 4 | [13 empty] | 0% | 0% | bar: 7 to 17
IDE 5 | [13 empty] | 0% | 0% | bar: 7 to 17
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0% | 0%
Boilers Summary | [13 empty] | 0 | 0
Service Hrs | [13 empty] | 0 | 0
WHB 21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HRSG 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Boiler 11 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
This Month Gals | [13 empty] | 0 | 0
WHB 21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HRSG 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Boiler 11 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TOTALS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
This Month LP STM LBS | [13 empty] | 0 | 0
WHB 21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HRSG 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Boiler 11 | [13 empty] | 0 | 0
TOTALS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
This Month HP STM LBS | [13 empty] | 0 | 0
WHB 21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HRSG 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Boiler 11 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TOTALS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Water Distribution | [13 empty] | 0 | 0
Total Water Produced |  | 90987333.3333 | 89121833.3333 | 82706166.6667 | 88049833.3333 | 87245333.3333 | 88737333.3333 | 98485500 | 87791833.3333 | 102458666.6667 | 96396333.3333 | 104287833.3333 |  | 1016268000 | 92388000
Total to Distribution Tank |  | 89206406.6667 | 87271346.6667 | 81464380 | 86830084.6667 | 85733049.6667 | 87158109.6667 | 96708970.3333 | 86222022.3333 | 100651625.6667 | 94420803.6667 | 102657288.6667 |  | 998324088 | 90756735.2727
Apparent Station Use |  | 1780926.6667 | 1850486.6667 | 1241786.6667 | 1219748.6667 | 1512283.6667 | 1579223.6667 | 1776529.6667 | 1569811 | 1807041 | 1975529.6667 | 1630544.6667 |  | 17943912 | 1631264.7273
Water to day Tank (Booster) Plus UPW Product |  | 1151333.3333 | 1244333.3333 | 1259000 | 1001333.3333 | 907333.3333 | 983333.3333 | 1165666.6667 | 889333.3333 | 1080333.3333 | 1298666.6667 | 1101666.6667 |  | 12082333.3333 | 1098393.9394
Water to the Demineralizer(regen) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Boilers Make Up |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 16 Noxwater |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 17 Noxwater |  | 8237911.2549 | 813283.4473 | 756803.4668 | 825476.5625 | 760796.3867 | 731756.3477 | 414203.125 | 51999.1455 | 304728.9124 | 191129.0588 | 433990.3564 |  | 13522078.064 | 1229279.824
Unit 19 Noxwater |  | 136276.123 | 214627.1973 | 360488.5254 | 39235.8398 | 57672.3633 | 27504.3945 | 86946.5332 | 25788.1718 | 0.47874 | 112497.9706 | 58103.653 |  | 1119141.2506 | 101740.1137
Unit 20 Noxwater |  | 0 | 0 | 0 | 0 | 0 | 15998.0469 | 345412.5977 | 479598.5107 | 409226.6846 | 677096.6797 | 297700.6836 |  | 2225033.2031 | 370838.8672
Total Wtr to NOX |  | 1007500 | 1094100 | 1093700 | 849900 | 812300 | 873400 | 1034200 | 796200 | 951200 | 1191100 | 1001600 |  | 10705200 | 973200
Station Wtr Warehouse & Eng. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Plant Service Water |  | 26900 | 17300 | 20400 | 50600 | 26700 | 20800 | 40500 | 34500 | 25900 | 43300 | 52300 |  | 359200 | 32654.5455
Admin. Off. Water |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
WTR to Fire Hydrants |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Total Water Used |  | 1780926.6667 | 1850486.6667 | 1241786.6667 | 1219748.6667 | 1512283.6667 | 1579223.6667 | 1776529.6667 | 1569811 | 1807041 | 1975529.6667 | 1630544.6667 |  | 17943912 | 1631264.7273
Unaccountable Water |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Steam Summary | [13 empty] | 0 | 0
LP Steam LBS | [13 empty] | 0 | 0
Total Steam Produced |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
From Steam Turbine 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
From Steam Turbine 11 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
[14 empty] | 0 | 0
HP STM to IDE's Ejectors | [13 empty] | 0 | 0
LP STM to IDE's Process |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Used Steam for Production |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
[14 empty] | 0 | 0
Others uses & Deareator |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HP Steam LBS | [13 empty] | 0 | 0
Total Steam Produced |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
To Steam Turbine 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
To Steam Turbine 11 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
From Steam Turbines |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HP STM to IDE's Ejectors |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
LP STM to IDE's Process | [13 empty] | 0 | 0
Used Steam for Production |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
[14 empty] | 0 | 0
Others uses & Deareator |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Boiler MUF from MUF Meters |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Boiler MUF from Desal Unit HPSTM Meters |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Boilers MUF per Desal Design Quantities |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
LPSTM to Desal/Condensate Return | [13 empty] | 0% | 0% | bar: 7 to 17
Boiler 10 MUF/HPSTM Generated | [13 empty] | 0% | 0%
Boiler 11 MUF/HPSTM Generated |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | 0% | 0%
WHB MUF / HP & LPSTM Generated |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | 0 | 0
[14 empty] | 0% | 0%
pag5 | [13 empty] | 0% | 0%
Feeder KWH | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 1360494.62 | 1358974.88 | 1203228 | 1236634 | 1144082 | 1184869.5 | 1129771.5 | 1075595.5 | 1232289.25 | 1226058.37 | 1364094.13 |  | 13516091.75 | 1228735.6136
Feeder # 2 (13 Kv) |  | 3241831.56 | 3157129.75 | 2883075 | 2859160.25 | 2675297.25 | 2639121 | 2549364.06 | 2331014.69 | 2640879.75 | 2581191 | 2845663.94 |  | 30403728.25 | 2763975.2955
Feeder # 3 (13(Kv) |  | 1111674 | 1126770 | 1084143 | 1086359 | 969113 | 1013913 | 945235 | 858463 | 941757 | 1320000 | 1430000 |  | 11887427 | 1080675.1818
Feeder # 4 (13 Kv) |  | 1542316.75 | 1558387 | 1484825 | 1499464.5 | 1392114.5 | 1357023.75 | 1284643.25 | 1184914 | 1324532.5 | 1313340.5 | 1432390.5 |  | 15373952.25 | 1397632.0227
Feeder # 5 (13 Kv) |  | 3890000 | 3720000 | 3630000 | 3620000 | 3230000 | 3090000 | 2920000 | 2700000 | 3080000 | 3800000 | 2850000 |  | 36530000 | 3320909.0909
Feeder # 6 (13 Kv) |  | 2272777 | 2244390 | 2070676 | 2085241 | 1905874 | 1980862 | 1833886 | 1668356 | 1867912 | 1790051 | 1790051 |  | 21510076 | 1955461.4545
Feeder # 9A (13 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 6B (24 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 8 (24 Kv) |  | 4999139.5 | 5863816.5 | 6954336 | 7030357 | 5578868 | 4475879 | 4310904 | 3964477.125 | 4487983.875 | 4312856.5 | 4685118.5 |  | 56663736 | 5151248.7273
Feeder # 9B (24Kv) |  | 4274225.25 | 2607787.671 | 0 | 0 | 1139488.6 | 1813588.4 | 1744764.5 | 1667335.5 | 1887485.5 | 1951085.5 | 2049093 |  | 19134853.921 | 2126094.8801
Feeder # 10A (24 Kv) |  | 0 | 832165 | 1843955 | 1859330 | 1776401 | 1880437 | 1763571 | 1653656 | 1804558 | 1726644 | 1927327 |  | 17068044 | 1706804.4
Feeder # 10 (24 Kv) |  | 1532181 | 1548799.5 | 1485914.75 | 1507122.75 | 1467690.5 | 1404689.5 | 1280436.5 | 1221431.5 | 1366458.25 | 1394038.625 | 1439499.125 |  | 15648262 | 1422569.2727
TOTALS |  | 24224639.68 | 24018220.301 | 22640152.75 | 22783668.5 | 21278928.85 | 20840383.15 | 19762575.81 | 18325243.315 | 20633856.125 | 21415265.495 | 21813237.195 |  | 237736171.171 | 21612379.1974
Feeder Planned Outages | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 2 (13 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 3 (13(Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 4 (13 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 5 (13 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 6 (13 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 6B (24 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feeder # 8 (24 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 9 (24Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 10 (24 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TOTALS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder Forced Outages | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 1 | 2 | 4 | 1 | 0 | 0 | 2 | 1 | 0 | 0 | 1 |  | 12 | 1.7143
Feeder # 2 (13 Kv) |  | 9 | 2 | 7 | 4 | 4 | 1 | 3 | 3 | 3 | 4 | 5 |  | 45 | 4.0909
Feeder # 3 (13(Kv) |  | 1 | 3 | 5 | 3 | 3 | 1 | 2 | 3 | 2 | 2 | 2 |  | 27 | 2.4545
Feeder # 4 (13 Kv) |  | 1 | 3 | 5 | 2 | 2 | 1 | 2 | 3 | 1 | 2 | 3 |  | 25 | 2.2727
Feeder # 5 (13 Kv) |  | 1 | 2 | 2 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 |  | 9 | 1.2857
Feeder # 6 (13 Kv) |  | 1 | 1 | 5 | 1 | 0 | 1 | 2 | 3 | 1 | 1 | 2 |  | 18 | 1.8
Feeder # 6B (24 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feeder # 8 (24 Kv) |  | 4 | 1 | 1 | 1 | 0 | 1 | 1 | 2 | 0 | 2 | 1 |  | 14 | 1.5556
Feeder # 9 (24Kv) |  | 2 | 1 | 0 | 0 | 0 | 2 | 2 | 2 | 1 | 1 | 1 |  | 12 | 1.5
Feeder # 10 (24 Kv) |  | 0 | 4 | 11 | 2 | 8 | 1 | 3 | 4 | 3 | 3 | 7 |  | 46 | 4.6
TOTALS |  | 20 | 19 | 40 | 15 | 17 | 8 | 18 | 22 | 11 | 15 | 23 |  | 208 | 18.9091
Feeder Total Outages HRS | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 0.41667 | 2.25 | 1.5833 | 1.9 | 0 | 0 | 4.5167 | 0.7 | 0 | 0 | 0.41667 |  | 11.7833 | 1.6833
Feeder # 2 (13 Kv) |  | 1.75 | 15.9167 | 3.45 | 2.9833 | 1.3667 | 0.083333 | 5.8333 | 1.5333 | 1.0833 | 0.98333 | 0.61667 |  | 35.6 | 3.2364
Feeder # 3 (13(Kv) |  | 0.43333 | 4.35 | 2.85 | 0.53333 | 1.2167 | 0.033333 | 4.8 | 1.2667 | 1 | 0.53333 | 0.96667 |  | 17.9833 | 1.6348
Feeder # 4 (13 Kv) |  | 0.81667 | 3.0167 | 3.1833 | 2.3333 | 1.2167 | 0.083333 | 5.0667 | 1.8667 | 0.33333 | 0.65 | 0.98333 |  | 19.55 | 1.7773
Feeder # 5 (13 Kv) |  | 0.41667 | 2.2333 | 0.81667 | 0.033333 | 0 | 0 | 0.4 | 0.7 | 0 | 0 | 0.41667 |  | 5.0167 | 0.71667
Feeder # 6 (13 Kv) |  | 0.83333 | 2.8167 | 3.05 | 1.9 | 0 | 0.1 | 5.5833 | 1.5667 | 0.31667 | 0.26667 | 1 |  | 17.4333 | 1.7433
Feeder # 6B (24 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feeder # 8 (24 Kv) |  | 1.3833 | 2.2833 | 0.73333 | 0.033333 | 0 | 0.083333 | 0.5 | 1.0167 | 0 | 0.41667 | 0.41667 |  | 6.8667 | 0.76296
Feeder # 9 (24Kv) |  | 2.1 | 2.8333 | 0 | 0 | 0 | 0.2 | 5.7667 | 1.35 | 0.3 | 0.26667 | 0.85 |  | 13.6667 | 1.7083
Feeder # 10 (24 Kv) |  | 0 | 6.5667 | 3.9167 | 2.1833 | 1.75 | 0.033333 | 5.8 | 1.5833 | 1.45 | 0.75 | 0.75 |  | 24.7833 | 2.4783
Feeder loss sales KWH | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 762.3527 | 4122.2696 | 2651.819 | 3166.1563 | 0 | 0 | 6900.4953 | 1121.5803 | 0 | 0 | 764.3697 |  | 19489.0429 | 2784.149
Feeder # 2 (13 Kv) |  | 7643.2539 | 69018.1735 | 13881.2487 | 11510.9801 | 5087.7679 | 295.6336 | 20146.2502 | 5330.9474 | 3850.9744 | 3530.0589 | 2360.5938 |  | 142655.8823 | 12968.7166
Feeder # 3 (13(Kv) |  | 647.8577 | 6626.7147 | 4308.4537 | 779.3106 | 1640.3935 | 45.4282 | 6137.8896 | 1621.1904 | 1267.5061 | 978.5026 | 1860.3921 |  | 25913.6392 | 2355.7854
Feeder # 4 (13 Kv) |  | 1694.8156 | 6344.4532 | 6594.0053 | 4717.4164 | 2356.3976 | 152.0134 | 8808.4525 | 3300.5961 | 593.6945 | 1186.726 | 1895.6739 |  | 37644.2445 | 3422.204
Feeder # 5 (13 Kv) |  | 2179.7602 | 11200.2876 | 4122.0366 | 162.1936 | 0 | 0 | 1570.737 | 2815.4327 | 0 | 0 | 1596.9965 |  | 23647.4442 | 3378.2063
Feeder # 6 (13 Kv) |  | 2548.5277 | 8529.1968 | 8808.9292 | 5338.8464 | 0 | 266.2807 | 13866.4216 | 3898.6095 | 795.3728 | 663.2275 | 2409.2207 |  | 47124.6328 | 4712.4633
Feeder # 6B (24 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feeder # 8 (24 Kv) |  | 9312.3096 | 18051.4316 | 7090.3416 | 314.9943 | 0 | 501.3867 | 2899.0612 | 6006.9327 | 0 | 2497.3112 | 2625.3046 |  | 49299.0735 | 5477.6748
Feeder # 9 (24Kv) |  | 12098.4944 | 9969.0556 | 0 | 0 | 0 | 487.6549 | 13629.1262 | 3356.3005 | 761.3899 | 722.892 | 2343.7113 |  | 43368.6248 | 5421.0781
Feeder # 10 (24 Kv) |  | 0 | 13791.6875 | 8127.3121 | 4435.8013 | 3575.995 | 62.9369 | 10060.3247 | 2884.6735 | 2668.3246 | 1453.6378 | 1452.5723 |  | 48513.2657 | 4851.3266
TOTALS |  | 36887.3718 | 147653.2701 | 55584.1463 | 30425.699 | 12660.5539 | 1811.3344 | 84018.7583 | 30336.2632 | 9937.2623 | 11032.3559 | 17308.8349 |  | 437655.85 | 39786.8955
Plant Feeder Total Planned Outages | [13 empty] | 0 | 0
Feeder # 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 6B (24 Kv)
Feeder # 8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TOTALS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Plant Feeder Total Forced Outages | [13 empty] | 0 | 0
Feeder # 1 |  | 0 | 2 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 |  | 8 | 2.6667
Feeder # 2 |  | 9 | 2 | 7 | 4 | 4 | 0 | 3 | 3 | 3 | 4 | 5 |  | 44 | 4.4
Feeder # 3 |  | 0 | 3 | 5 | 3 | 3 | 0 | 2 | 3 | 2 | 2 | 2 |  | 25 | 2.7778
Feeder # 4 |  | 0 | 3 | 5 | 2 | 2 | 0 | 2 | 3 | 0 | 2 | 3 |  | 22 | 2.75
Feeder # 5 |  | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 2
Feeder # 6 |  | 0 | 0 | 5 | 0 | 0 | 0 | 2 | 3 | 0 | 0 | 2 |  | 12 | 3
Feeder # 6B (24 Kv)
Feeder # 8 |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 |  | 8 | 2.6667
Feeder # 9 |  | 2 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 0 | 0 | 0 |  | 8 | 2
Feeder # 10 |  | 0 | 4 | 11 | 2 | 8 | 0 | 3 | 4 | 3 | 3 | 7 |  | 45 | 5
TOTALS |  | 15 | 16 | 39 | 11 | 17 | 2 | 16 | 20 | 8 | 13 | 19 |  | 176 | 16
Plant Feeder Total Outages Time | [13 empty] | 0 | 0
Feeder # 1 |  | 0.41667 | 2.25 | 1.5833 | 1.9 | 0 | 0 | 4.5167 | 0.7 | 0 | 0 | 0.41667 |  | 11.7833 | 1.6833
Feeder # 2 |  | 1.75 | 15.9167 | 3.45 | 2.9833 | 1.3667 | 0.083333 | 5.8333 | 1.5333 | 1.0833 | 0.98333 | 0.61667 |  | 35.6 | 3.2364
Feeder # 3 |  | 0.43333 | 4.35 | 2.85 | 0.53333 | 1.2167 | 0.033333 | 4.8 | 1.2667 | 1 | 0.53333 | 0.96667 |  | 17.9833 | 1.6348
Feeder # 4 |  | 0.81667 | 3.0167 | 3.1833 | 2.3333 | 1.2167 | 0.083333 | 5.0667 | 1.8667 | 0.33333 | 0.65 | 0.98333 |  | 19.55 | 1.7773
Feeder # 5 |  | 0.41667 | 2.2333 | 0.81667 | 0.033333 | 0 | 0 | 0.4 | 0.7 | 0 | 0 | 0.41667 |  | 5.0167 | 0.71667
Feeder # 6 |  | 0.83333 | 2.8167 | 3.05 | 1.9 | 0 | 0.1 | 5.5833 | 1.5667 | 0.31667 | 0.26667 | 1 |  | 17.4333 | 1.7433
Feeder # 6B (24 Kv)
Feeder # 8 |  | 1.3833 | 2.2833 | 0.73333 | 0.033333 | 0 | 0.083333 | 0.5 | 1.0167 | 0 | 0.41667 | 0.41667 |  | 6.8667 | 0.76296
Feeder # 9 |  | 2.1 | 2.8333 | 0 | 0 | 0 | 0.2 | 5.7667 | 1.35 | 0.3 | 0.26667 | 0.85 |  | 13.6667 | 1.7083
Feeder # 10 |  | 0 | 6.5667 | 3.9167 | 2.1833 | 1.75 | 0.033333 | 5.8 | 1.5833 | 1.45 | 0.75 | 0.75 |  | 24.7833 | 2.4783
TOTALS | [13 empty] | 0 | 0
Plant Feeder Total Loss sales | [13 empty] | 0 | 0
Feeder # 1 |  | 762.3527 | 4122.2696 | 2651.819 | 3166.1563 | 0 | 0 | 6900.4953 | 1121.5803 | 0 | 0 | 764.3697 |  | 19489.0429 | 2784.149
Feeder # 2 |  | 7643.2539 | 69018.1735 | 13881.2487 | 11510.9801 | 5087.7679 | 295.6336 | 20146.2502 | 5330.9474 | 3850.9744 | 3530.0589 | 2360.5938 |  | 142655.8823 | 12968.7166
Feeder # 3 |  | 647.8577 | 6626.7147 | 4308.4537 | 779.3106 | 1640.3935 | 45.4282 | 6137.8896 | 1621.1904 | 1267.5061 | 978.5026 | 1860.3921 |  | 25913.6392 | 2355.7854
Feeder # 4 |  | 1694.8156 | 6344.4532 | 6594.0053 | 4717.4164 | 2356.3976 | 152.0134 | 8808.4525 | 3300.5961 | 593.6945 | 1186.726 | 1895.6739 |  | 37644.2445 | 3422.204
Feeder # 5 |  | 2179.7602 | 11200.2876 | 4122.0366 | 162.1936 | 0 | 0 | 1570.737 | 2815.4327 | 0 | 0 | 1596.9965 |  | 23647.4442 | 3378.2063
Feeder # 6 |  | 2548.5277 | 8529.1968 | 8808.9292 | 5338.8464 | 0 | 266.2807 | 13866.4216 | 3898.6095 | 795.3728 | 663.2275 | 2409.2207 |  | 47124.6328 | 4712.4633
Feeder # 6B (24 Kv)
Feeder # 8 |  | 9312.3096 | 18051.4316 | 7090.3416 | 314.9943 | 0 | 501.3867 | 2899.0612 | 6006.9327 | 0 | 2497.3112 | 2625.3046 |  | 49299.0735 | 5477.6748
Feeder # 9 |  | 12098.4944 | 9969.0556 | 0 | 0 | 0 | 487.6549 | 13629.1262 | 3356.3005 | 761.3899 | 722.892 | 2343.7113 |  | 43368.6248 | 5421.0781
Feeder # 10 |  | 0 | 13791.6875 | 8127.3121 | 4435.8013 | 3575.995 | 62.9369 | 10060.3247 | 2884.6735 | 2668.3246 | 1453.6378 | 1452.5723 |  | 48513.2657 | 4851.3266
TOTALS |  | 36887.3718 | 147653.2701 | 55584.1463 | 30425.699 | 12660.5539 | 1811.3344 | 84018.7583 | 30336.2632 | 9937.2623 | 11032.3559 | 17308.8349 |  | 437655.85 | 39786.8955
Line Feeder Total Planned Outages | [13 empty] | 0 | 0
Feeder # 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 6B (24 Kv)
Feeder # 8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TOTALS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Line Feeder Total Forced Outages | [13 empty] | 0 | 0
Feeder # 1 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 1 |  | 4 | 1
Feeder # 2 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 1 | 1
Feeder # 3 |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 2 | 1
Feeder # 4 |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 |  | 3 | 1
Feeder # 5 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 |  | 5 | 1
Feeder # 6 |  | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 0 |  | 6 | 1
Feeder # 6B (24 Kv)
Feeder # 8 |  | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 1 |  | 6 | 1
Feeder # 9 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | 4 | 1
Feeder # 10 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 1 | 1
TOTALS |  | 5 | 3 | 1 | 4 | 0 | 6 | 2 | 2 | 3 | 2 | 4 |  | 32 | 3.2
Line Feeder Total Outages Time | [13 empty] | 0 | 0
Feeder # 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 6B (24 Kv)
Feeder # 8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TOTALS | [13 empty] | 0 | 0
Line Feeder Total Loss sales | [13 empty] | 0 | 0
Feeder # 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 6B (24 Kv)
Feeder # 8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Feeder # 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TOTALS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
pag6 | [13 empty] | 0 | 0
Units Outages | [13 empty] | 0 | 0
Unit 10 ST | [13 empty] | 11 | 1 | bar: 7 to 17
Unit 11 ST | [13 empty] | 11 | 1 | bar: 7 to 17
Unit 11 BLR | [13 empty] | 11 | 1 | bar: 7 to 17
Unit 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 17 |  | 1 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4 | 1.3333
Unit 19 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 20 | [13 empty] | 11 | 1 | bar: 7 to 17
Aggreko |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HRSG 21 | [13 empty] | 11 | 1 | bar: 7 to 17
HRSG 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Units Outages Duration | [13 empty] | 0 | 0
Unit 10 ST |  | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 | 744 | 720 | 744 |  | 8040 | 730.9091
Unit 11 ST |  | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 | 744 | 720 | 744 |  | 8040 | 730.9091
Unit 11 BLR |  | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 | 744 | 720 | 744 |  | 8040 | 730.9091
Unit 16 |  | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 | 744 | 720 | 744 |  | 8040 | 730.9091
Unit 17 |  | 0 | 0 | 26.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.65 | 26.65
Unit 19 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 20 |  | 744 | 744 | 720 | 744 | 720 | 723.3167 | 0 | 0 | 0 | 0 | 0 |  | 4395.3167 | 732.5528
Aggreko |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HRSG 21 |  | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 | 744 | 720 | 744 |  | 8040 | 730.9091
HRSG 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit Planned Outages | [13 empty] | 0 | 0
Unit 10 ST | [13 empty] | 11 | 1 | bar: 7 to 17
Unit 11 ST | [13 empty] | 11 | 1 | bar: 7 to 17
Unit 11 BLR | [13 empty] | 11 | 1 | bar: 7 to 17
Unit 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 17 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 1
Unit 19 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 20 | [13 empty] | 11 | 1 | bar: 7 to 17
Aggreko |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HRSG 21 | [13 empty] | 11 | 1 | bar: 7 to 17
HRSG 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Unit Planned Outages Duration | [13 empty] | 0 | 0
Unit 10 ST |  | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 | 744 | 720 | 744 |  | 8040 | 730.9091
Unit 11 ST |  | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 | 744 | 720 | 744 |  | 8040 | 730.9091
Unit 11 BLR |  | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 | 744 | 720 | 744 |  | 8040 | 730.9091
Unit 16 |  | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 | 744 | 720 | 744 |  | 8040 | 730.9091
Unit 17 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 19 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 20 |  | 744 | 744 | 720 | 744 | 720 | 723.3167 | 0 | 0 | 0 | 0 | 0 |  | 4395.3167 | 732.5528
Aggreko |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HRSG 21 |  | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 | 744 | 720 | 744 |  | 8040 | 730.9091
HRSG 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Unit Forced Outages |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 10 ST |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 11 ST |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 11 BLR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 17 |  | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 2
Unit 19 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 20 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Aggreko |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HRSG 21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HRSG 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Unit Forced Outages Duration |  | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 2
Unit 10 ST |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 11 ST |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 11 BLR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 17 |  | 0 | 0 | 26.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 26.65 | 26.65
Unit 19 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 20 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Aggreko |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HRSG 21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HRSG 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plant Power Distribution | [13 empty] | 0 | 0
Total 13KV Feeders |  | 13419093.93 | 13165651.63 | 12355947 | 12386858.75 | 11316480.75 | 11265789.25 | 10662899.81 | 9818343.19 | 11087370.5 | 12030640.87 | 11712199.57 |  | 129221275.25 | 11747388.6591
Total 24KV Feeders |  | 10805545.75 | 10852568.671 | 10284205.75 | 10396809.75 | 9962448.1 | 9574593.9 | 9099676 | 8506900.125 | 9546485.625 | 9384624.625 | 10101037.625 |  | 108514895.921 | 9864990.5383
Feeder Totals |  | 24224639.68 | 24018220.301 | 22640152.75 | 22783668.5 | 21278928.85 | 20840383.15 | 19762575.81 | 18325243.315 | 20633856.125 | 21415265.495 | 21813237.195 |  | 237736171.171 | 21612379.1974
Total Generation |  | 25719989.5 | 25797063.5 | 24243512.5 | 24404586 | 22938640 | 22207306.406 | 21720886.844 | 19883892.25 | 22354913.25 | 21899651.5 | 24293725.5 |  | 255464167.25 | 23224015.2045
24 KV BUS at XFMR-1 (T1) |  | 66909.75 | 391221.84 | 1276007.57 | 55735.12 | 63357.25 | 36349 | 26179.75 | 144837 | 262627.5 | 2408580.25 | 34041.5 |  | 4765846.53 | 433258.7755
24 KV BUS at XFMR-2 (T2) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
24 KV BUS at XFMR-3 (T3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
XFMR T1 in |  | 66510 | 389244 | 1270567 | 55447 | 62657 | 36161 | 25980 | 144012 | 261428 | 2397687 | 33866
XFMR T1 out |  | 4351087 | 4122766 | 4142281 | 5145701 | 4707082 | 5536054 | 7918545 | 4548740 | 4835111 | 3403898 | 4608722
XFMR T3 in |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XFMR T3 out |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XFMR T4in (from #16) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XFMR T4 out ( |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XFMR T5 in (from #20) |  | 0 | 99999416 | 584 | 0 | 0 | 81566 | 2583105 | 0 | 26 | 82 | 0
XFMR T5 out |  | 5558411 | 5172388 | 4438906 | 4536047 | 4221366 | 3120464 | 1798985 | 3598643 | 4057617 | 3882087 | 4319525
T1 &T3&T4 & T5 Available |  | 9976008 | 109683814 | 9852338 | 9737195 | 8991105 | 8774245 | 12326615 | 8291395 | 9154182 | 9683754 | 8962113 |  | 205432764 | 18675705.8182
T1 &T3 & T4 & T5 Losses |  | 47669.07 | 366338.699 | 251331.5 | 237737.5 | 312477.1 | 41634.314 | 368462.654 | 117165.435 | 36703.875 | 1171060.495 | 804645.305 |  | 3755225.947 | 341384.177
Net Distributed |  | 25672320.43 | 25430724.801 | 23992181 | 24166848.5 | 22626162.9 | 22165672.092 | 21352424.19 | 19766726.815 | 22318209.375 | 20728591.005 | 23489080.195 |  | 251708941.303 | 22882631.0275
Line Department |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Water Department |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Power Plant Services |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Administration & General |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Plant Station Service |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Net Available from Bus |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Wapa KWH From Dist |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
SwitchGear Bkr1 SS |  | 1126712.5 | 1097708.5 | 1046123 | 1076282.5 | 1059253 | 1087062.87 | 1218442.13 | 1079256.5 | 1280661.5 | 1246724 | 1291947 |  | 12610173.5 | 1146379.4091
SwitchGear Bkr3 SS |  | 301288.25 | 306636 | 302425.25 | 302817.5 | 284381.05 | 317414.7 | 369246.25 | 361867 | 402011.75 | 408122.5 | 382096 |  | 3738306.25 | 339846.0227
Total Station Service Power |  | 1437840.75 | 1408424.5 | 1350288.25 | 1381140 | 1345434.05 | 1406517.57 | 1588768.38 | 1441303.5 | 1683513.25 | 1655146.5 | 1674943 |  | 16373319.75 | 1488483.6136
Net KWH Available for Sale |  | 24234479.68 | 24022300.301 | 22641892.75 | 22785708.5 | 21280728.85 | 20759154.522 | 19763655.81 | 18325423.315 | 20634696.125 | 19073444.505 | 21814137.195 |  | 235335621.553 | 21394147.4139
Plant Unaccountable |  | 0 | 0 | 0 | 0 | 0 | -83268.628 | 0 | 0 | 0 | -2342120.99 | 0
Peak Load: |  | 41080 | 41790 | 40070 | 39340 | 39400 | 37330 | 38220 | 35500 | 36800 | 37380 | 2005-04-08 |  | 425360 | 38669.0909
Day |  | Thursday | Sunday | Tuesday | Saturday | Sunday | Friday | Saturday | Wednesday | Wednesday | Wednesday | Tuesday |  |  | 0
Date |  | 2020-07-02 | 2020-08-16 | 2020-09-29 | 2020-10-10 | 2020-11-08 | 2021-12-17 | 2021-01-16 | 2021-02-03 | 2021-03-24 | 2021-04-14 | 2021-05-18
Hour |  | 19:20 | 19:21 | 19:00 | 18:39 | 19:00 | 18:00 | 20:00 | 0.78264 | 0.81181 | 19:00 | 19:12
Min Load |  | 27650 | 26320 | 25710 | 25910 | 24450 | 23490 | 23290 | 23290 | 23800 | 24370 | 24970 |  | 273250 | 24840.9091
Day |  | Sunday | Wednesday | Sunday | Thursday | Sunday | Tuesday | Thursday | Sunday | Sunday | Sunday | Saturday
Date |  | 2020-07-19 | 2020-08-05 | 2020-09-20 | 2020-10-29 | 2020-11-29 | 2021-12-07 | 2021-01-07 | 44234 | 44269 | 2021-04-11 | 2021-05-15
Hour |  | 6:00 | 6:00 | 4:00 | 3:00 | 7:00 | 4:00 | 4:00 | 0.20833 | 0.16667 | 4:00 | 6:00 |  |  | 4:49
Pag 7
No 6 Fuel For Power |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
No 6 Fuel For Water |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
No 2 Fuel For Power |  | 5520.1249 | 9234.3241 | 16758.6572 | 1935.0103 | 2188.4473 | 2056.614 | 4149.3782 | 1607.2953 | 2355.5808 | 18615.4767 | 2344.0406 |  | 66764.9496 | 6069.5409
No 2 Fuel For Water |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
O&M Factor for Water |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
BLR11FUEL2COST |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Firing | [13 empty] | 0 | 0
WHBSFCAE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Power Boilers | [13 empty] | 0 | 0
[14 empty] | 0 | 0
TPBSFC | [13 empty] | 0 | 0
BLR11FUELCOST |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Combined Cycle | [13 empty] | 0 | 0
WHB, 16 & 17 | [13 empty] | 0 | 0
TGTFC | [13 empty] | 0 | 0
GEN161720FUELCOST |  | 1999545.5291 | 1924719.682 | 1614411.4254 | 1804814.6582 | 1759979.7993 | 1914831.8574 | 2474540.2423 | 1996028.5493 | 2457135.4513 | 2638643.8819 | 2298213.7497 |  | 22882864.8258 | 2080260.4387
Simple Cycle | [13 empty] | 0 | 0
12 & 14 & 22 | [13 empty] | 0 | 0
GEN 19FUELCOST |  | 343756.9591 | 495210.025 | 787472.5538 | 88884.4036 | 129727.8244 | 63153.6403 | 182272.3202 | 63584.2339 | 408.4237 | 254191.2325 | 129228.7298 |  | 2537890.3462 | 230717.3042
DIESEL | [13 empty] | 0 | 0
7 St. John | [13 empty] | 0 | 0
DIESEL_EMER. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
GT Fuel Allocation | [13 empty] | 0 | 0
HP Stm from WHB | [13 empty] | 0 | 0
GTFCAE | [13 empty] | 0 | 0
WHBHPSTMCOST |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
whb Benefit | [13 empty] | 0 | 0
Equalization to Water | [13 empty] | 0 | 0
WHBBECW | [13 empty] | 0 | 0
WHBBENCOSTWTR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Extraction Benefit | [13 empty] | 0 | 0
Equalization to Water | [13 empty] | 0 | 0
BECW | [13 empty] | 0 | 0
BENEQFCOSTWTR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Gas Turbine | [13 empty] | 0 | 0
Power Allocation | [13 empty] | 0 | 0
GTFCA | [13 empty] | 0 | 0
GEN161720ADJFCOST |  | 1999545.5291 | 1924719.682 | 1614411.4254 | 1804814.6582 | 1759979.7993 | 1914831.8574 | 2474540.2423 | 1996028.5493 | 2457135.4513 | 2638643.8819 | 2298213.7497 |  | 22882864.8258 | 2080260.4387
Extraction Incremental | [13 empty] | 0 | 0
to Water | [13 empty] | 0 | 0
FCAWI | [13 empty] | 0 | 0
INCRFUELCOSTWTR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
GT Fuel Allocation | [13 empty] | 0 | 0
LP Stm from WHB | [13 empty] | 0 | 0
WHBFCAW | [13 empty] | 0 | 0
WHBLPSTMCOST |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Electrc Power | [13 empty] | 0 | 0
Generation | [13 empty] | 0 | 0
TOTFUELCOSTPWR |  | 3713314.5045 | 3744752.5614 | 3562453.9143 | 3315497.8093 | 3275251.6783 | 3496583.1529 | 4188975.5048 | 3662267.9831 | 4312300.3544 | 4027455.6774 | 4235553.1644 |  | 41534406.3047 | 3775855.1186
RO Electricity cost |  | 70963.9268 | 74207.1698 | 62238.2739 | 65426.4231 | 65607.1959 | 78153.5202 | 108141.6507 | 85982.2109 | 114714.3319 | 95968.8535 | 100888.5583 |  | 922292.1149 | 83844.7377
UPW Electicity Cost |  | 2771.5908 | 2670.0228 | 2442.0318 | 2235.9573 | 2189.1774 | 2524.0904 | 3269.6675 | 2751.7675 | 3478.5179 | 2852.6114 | 2499.9646 |  | 29685.3994 | 2698.6727
RO Annex Electricity cost |  | 96033.7397 | 88297.0049 | 89701.1334 | 84224.1728 | 89743.4627 | 98096.1286 | 137721.6401 | 122647.8916 | 145855.2444 | 135933.1611 | 134009.6224
TOTFUELCSRWTR |  | 166997.6665 | 162504.1747 | 151939.4073 | 149650.5959 | 155350.6585 | 176249.6488 | 245863.2908 | 208630.1026 | 260569.5762 | 231902.0145 | 234898.1807 |  | 2144555.3166 | 194959.5742
Pag8 | [13 empty] | 0 | 0
No 2 BBLS | [13 empty] | 0 | 0
Inventory-Beginning of Month |  | 39740.5629 | 34220.4379 | 57168.2338 | 40409.5766 | 38474.5663 | 36286.119 | 34229.505 | 30080.1268 | 28472.8314 | 26117.2506 | 19559.2938 |  | 384758.504 | 34978.0458
Received During Month |  | 0 | 32182.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12057.52 | 0 |  | 44239.64 | 22119.82
Consumed During Month |  | 5520.1249 | 9234.3241 | 16758.6572 | 1935.0103 | 2188.4473 | 2056.614 | 4149.3782 | 1607.2953 | 2355.5808 | 18615.4767 | 2344.0406 |  | 66764.9496 | 6069.5409
Inventory-End of Month |  | 34220.4379 | 57168.2338 | 40409.5766 | 38474.5663 | 36286.119 | 34229.505 | 30080.1268 | 28472.8314 | 26117.2506 | 19559.2938 | 17215.2533 |  | 362233.1944 | 32930.2904
Calorific Value (BTU/GAL) |  | 136784.2908 | 136999.0879 | 136999.0879 | 136999.0879 | 136999.0879 | 136999.0879 | 136999.0879 | 136999.0879 | 136999.0879 | 137924.0668 | 137924.0668 |  | 1508625.1279 | 137147.7389
Calorific Value (BTU/GAL) |  | 136784.2908 | 136999.0879 | 136999.0879 | 136999.0879 | 136999.0879 | 136999.0879 | 136999.0879 | 136999.0879 | 136999.0879 | 137924.0668 | 137924.0668 |  | 1508625.1279 | 137147.7389
No 6 BBLS | [13 empty] | 0 | 0
Inventory-Beginning of Month |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Received During Month |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Consumed During Month |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Inventory-End of Month |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Calorific Value (BTU/GAL) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
PROPANE
Propane Value (BTU/Gal) |  | 91735 | 91735 | 91735 | 91647 | 91647 | 91425 | 91425 | 91425 | 91425 | 91653 | 91415
End of Month- Fuel in Tanks | [13 empty] | 0 | 0
No 2 BBLS | [13 empty] | 0 | 0
Tank 1 #2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Tank 2 #2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Tank 5 #2 |  | 8440.91 | 37021.4 | 30852.38 | 28860.59 | 26657.03 | 24785.45 | 20278.4 | 18987.72 | 16601.33 | 4299.44 | 4334.54 |  | 221119.19 | 20101.7445
Tank 6 #2 |  | 17422.64 | 11760.45 | 1141.19 | 1124.68 | 1127.88 | 944.64 | 1240.9 | 944.64 | 944.64 | 6699.67 | 4186.88 |  | 47538.21 | 4321.6555
TOTAL |  | 34220.44 | 57168.23 | 40409.58 | 38474.57 | 36286.12 | 34229.5 | 30080.13 | 28472.83 | 26117.25 | 19559.29 | 17215.25 |  | 362233.19 | 32930.29
No 6 BBLS | [13 empty] | 0 | 0
Tank 3 #2 |  | 4452.57 | 4450.29 | 4453.2 | 4451.44 | 4450.51 | 4444.46 | 4450.11 | 4425.75 | 4456.57 | 4377.5 | 4457.52 |  | 48869.92 | 4442.72
Tank 4 #6 |  | 3904.33 | 3936.1 | 3962.8 | 4037.85 | 4050.7 | 4054.95 | 4110.72 | 4114.71 | 4114.71 | 4182.69 | 4236.31 |  | 44705.87 | 4064.17
Tank 7 #6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TOTAL |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
Fuel Shipments | [13 empty] | 0 | 0
Date(1) |  | 0 | 2020-08-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2021-04-14 | 0 |  | 2141-12-03 | 2020-12-16
No2 BBLS |  | 0 | 32182.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12057.52 | 0 |  | 44239.64 | 22119.82
Date(2) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
No2 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Date(3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
No2 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Date(4) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
No2 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Date(5) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
No2 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Date(6) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
No2 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Date(7) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
No2 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Date(8) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
No2 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Date(9) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
No2 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TOTAL SHIPMENTS No 2 |  | 0 | 32182.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12057.52 | 0 |  | 44239.64 | 22119.82
Date(1) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
No6 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Date(2) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
No6 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Date(3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
No6 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Date(4) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
No6 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Date(5) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
No6 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Date(6) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
No6 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Date(7) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
No6 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Date(8) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
No6 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TOTAL SHIPMENTS No 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
[14 empty] | 0 | 0
Fuel Allocations Amount | [13 empty] | 0 | 0
Electric Power Generation |  | 3713314.5045 | 3744752.5614 | 3562453.9143 | 3315497.8093 | 3275251.6783 | 3496583.1529 | 4188975.5048 | 3662267.9831 | 4312300.3544 | 4027455.6774 | 4235553.1644 |  | 41534406.3047 | 3775855.1186
Water Production |  | 166997.6665 | 162504.1747 | 151939.4073 | 149650.5959 | 155350.6585 | 176249.6488 | 245863.2908 | 208630.1026 | 260569.5762 | 231902.0145 | 234898.1807 |  | 2144555.3166 | 194959.5742
Total #2 Fuel Cost |  | 426605.2954 | 639765.748 | 1161061.1421 | 134059.983 | 151618.4179 | 142478.9617 | 287462.368 | 111350.8443 | 163190.9234 | 1323140.361 | 166608.3951 |  | 4707342.4398 | 427940.2218
BBLS No. 6 for Power |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
BBLS No.6 for Water |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
BBLS No. 2 for Power |  | 5520.1249 | 9234.3241 | 16758.6572 | 1935.0103 | 2188.4473 | 2056.614 | 4149.3782 | 1607.2953 | 2355.5808 | 18615.4767 | 2344.0406 |  | 66764.9496 | 6069.5409
BBLS No.2 for Water |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
No. 6 BBL Cost |  | 71.9034 | 71.9034 | 71.9034 | 71.9034 | 71.9034 | 71.9034 | 71.9034 | 71.9034 | 71.9034 | 71.9034 | 71.9034 |  | 790.9373 | 71.9034
No. 2 BBL Cost |  | 77.2818 | 69.2813 | 69.2813 | 69.2813 | 69.2813 | 69.2784 | 69.2784 | 69.2784 | 69.2784 | 71.0774 | 71.0774 |  | 773.6754 | 70.3341
Propane Cost per Bbl |  | 38.3544 | 38.262 | 37.5354 | 38.1612 | 39.7362 | 43.26 | 52.8234 | 52.1514 | 55.0662 | 51.0678 | 50.82
Propane Consumed
Unit 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Unit 17 |  | 2098879.9746 | 1954076.7936 | 1388410.9176 | 1936648.7771 | 1837109.4026 | 1757927.9258 | 926509.918 | 152377.8603 | 518917.008 | 0 | 936478.9135 |  | 13507337.491
Unit 20 |  | 0 | 0 | 0 | 0 | 0 | 24117.2548 | 957365.5646 | 1416650.0361 | 1231028.0394 | 1290973.5614 | 931979.0075 |  | 5852113.4638 | 975352.244
Aggreko |  | 1683103.0254 | 1632631.2064 | 1468624.0824 | 1729528.2229 | 1628680.5974 | 1645482.8194 | 1413712.5174 | 1458714.1036 | 1613397.9526 | 1123877.4386 | 1688437.079 |  | 17086189.0452
No. 2 Units BBLS No. 2 Consumed | [13 empty] | 0 | 0
Unit 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 11 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Unit 17 |  | 1072.0288 | 2086.5049 | 5392.3457 | 652.0604 | 315.967 | 443.7555 | 873.1619 | 337.2299 | 1220.2799 | 6040.3176 | 380.8956 |  | 18814.5473 | 1710.4134
Unit 19 |  | 4448.0961 | 7147.8192 | 11366.3115 | 1282.9499 | 1872.4803 | 911.5919 | 2631.0115 | 917.8075 | 5.8954 | 3576.2578 | 1818.14 |  | 35978.361 | 3270.7601
Unit 20 |  | 0 | 0 | 0 | 0 | 0 | 701.2667 | 645.2048 | 352.2579 | 1129.4056 | 8998.9014 | 145.005 |  | 11972.0413 | 1995.3402
Diesel Emergency |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Total No. 2 Consumed |  | 5520.1249 | 9234.3241 | 16758.6572 | 1935.0103 | 2188.4473 | 2056.614 | 4149.3782 | 1607.2953 | 2355.5808 | 18615.4767 | 2344.0406 |  | 66764.9496 | 6069.5409
Note on I673: Nicholson: negative

## PR-Pag1
May - 2021
Production Summary |  |  |  |  | Generating Units Heat Rate |  | FYTD | This Month
|  | FYTD | FYTD |  | (Gross Energy in KWH Produced) | This Month | AVG. | %
Item | This Month | AVG. | TOTAL | Units | Units | BTU/KWH | BTU/KWH | Efficiency
Total System Gross Generation** | 24293.7255 | 23224.0152 | 255464.1672 | MWH
Gross Power Plant Generation | 23621.77 | 22574.4555 | 248319.01 | MWH
Gross Water Production | 104287.8333 | 92388 | 1016268 | KGAL
System Load Factor | 82.57% | 79.79% |  | % | Unit 10-Steam (10 MW) + WHBs* | N/A | N/A | N/A
Total Propane Fuel Cost | 4303842.95 | 3542874.471 | 38971619.1815 | $ | Unit 11-Steam (19.1 MW) + WHBs | N/A | N/A | N/A
Total No. 2 Fuel Cost | 166608.3951 | 427940.2218 | 4707342.4398 | $ | Unit 16-Gas Turbine (22.5 MW) | 0 | 0 | 0%
Power Fuel Cost (Internal) | 0.18925 | 0.17725 |  | $/KWH | Unit 17-Gas Turbine (21.9 MW) | 16711.71 | 19402.16 | 20.42%
Power Fuel Cost (to bus) | 0.20494 | 0.18523 |  | $/KWH | Unit 19-Gas Turbine (24.5 MW) | 19871.96 | 22374.29 | 17.17%
Water Fuel Cost (Internal) | 2.2524 | 2.0942 |  | $/KGAL | Unit 20_Gas Turbine (24.5 MW) | 22417.57 | 24435.78 | 15.22%
Water Fuel Cost (to Distribution) | 2.2882 | 2.132 |  | $/KGAL | Aggreko (20.0 MW) | 11025.54 | 11028.26 | 30.95%
Total Power Fuel Cost | 4235553.1644 | 3775855.1186 | 41534406.3047 | $ | Total Electric Generation Only | 14339.83 | 14993.09 | 23.79%
Total Water Cost | 234898.1807 | 194959.5742 | 2144555.3166 | $ | *Note:Total Electric Generation includes values of steam provided to STG #10 and #11 by HRSGs
Propane consumed | 84687.9762 | 78886.6667 | 867753.3333 | BBLS
No. 2 Fuel Consumed | 2344.0406 | 6069.5409 | 66764.9496 | BBLS
[5 empty] | Power Units Availability |  | FYTD
No. 2 Fuel Received | 0 | 22119.82 | 44239.64 | BBLS |  | This Month | AVG.
[5 empty] | Unit | Percent (%) | Percent (%)
EOM No. 2 Fuel On Hand* | 8.6076 | 16.4651 |  | DAYS
Plant Water Use ( Internal | 1896.7362 | 3083.6192 | 33919.8114 | $ | Unit 10 | 0% | 0%
Plant Power Use (Internal) | 297088.0142 | 248456.4959 | 2733021.4547 | $ | Unit 11 | 0% | 0%
7SEAS RO 1 Electricity Cost | 100888.5583 |  |  | $ | Unit 16 | 0% | 0%
7SEAS UPW Electricity Cost | 2499.9646 |  |  | $ | Unit 17 | 100% | 99.66%
7SEAS RO 2 Electricity Cost | 134009.6224 |  |  | $ | Unit 19 | 100% | 100%
**Note: Includes power generated by solar |  |  |  |  | Unit 20 | 100% | 45.71%
*Note: Based on 2000Bbl/day consumption |  |  |  |  | Aggreko | 100% | 100%
[5 empty] | HRSG 21 | 0% | 0%
[5 empty] | HRSG 24 | 100% | 100%

## PR-Pag2
May - 2021
Power Generation - Station Power |  | FYTD | TOTAL | Generating Units Average Loading |  |  | FYTD | Utilization
Item | This Month | Monthly | FYTD |  |  | This Month | AVG. | Factor
| KWH | AVG. | KWH | (KWH / Operating Hours) |  | KW | KW | Percent
Steam Turbine Generation | 0 | 0 | 0 | Unit 10 |  | 0 | 0 | 0%
Gas Turbine Generation | 23621770 | 22574455.4545 | 248319010 | Unit 11 |  | 0 | 0 | 0%
Diesel Generation | 0 | 0 | 0 | Unit 16 |  | 0 | 0 | 0%
Total Generation | 23621770 | 22574455.4545 | 248319010 | Unit 17 |  | 12980.9289 | 12176.242 | 59.27%
Steam Station Power | 0 | 0 | 0 | Unit 19 |  | 9888.0597 | 8757.8708 | 40.36%
Gas Turbine Station Power | 97330 | 75774.5455 | 833520 | Unit 20 |  | 12214.895 | 10820.8362 | 49.86%
Aggreko Station Service | 410 | 1922.7273 | 21150 | Aggreko |  | 0 | 19055.6461 | 0%
Total Gen. Plant Station Power | 97330 | 75774.5455 | 833520 | Diesel |  | 0 | 0 | 0%
Total Service / Gross Output | 0.412% | 0.3462%
IPP1 | 671955.5 | 649559.75 | 7145157.25
Total System Generation | 24293725.5 | 22574455.4545 | 248319010
Generating Units Station Power
Generating Units Operating Hours |  | FYTD | TOTAL |  |  | FYTD | TOTAL | This Month | FYTD | FYTD
| This Month | Monthly | FYTD |  | This Month | AVG. | FYTD | SS Power | AVG. | SS Power
Unit | HRS | AVG. | HRS | Unit | KWH | KWH | KWH | KWH | KWH | KWH
Unit 10 | 0 | 0 | 0 | Unit 10 | 0 | 0 | 0 | 0 | 0 | 0
Unit 11 | 0 | 0 | 0 | Unit 11 | 0 | 0 | 0 | 0 | 0 | 0
Unit 16 | 0 | 0 | 0 | Unit 16 | 0 | 0 | 0 | 0 | 0 | 0
Unit 17 | 404.8 | 504.5818 | 5550.4 | Unit 17 | 5254680 | 6172352.7273 | 67895880 | 12300 | 10094.5455 | 111040
Unit 19 | 53.6 | 99.4545 | 1094 | Unit 19 | 530000 | 947000 | 9470000 | 28000 | 29367.2727 | 323040
Unit 20 | 314.2 | 422.9667 | 2537.8 | Unit 20 | 3837920 | 4829506.6667 | 28977040 | 57030 | 36312.7273 | 399440
Aggreko | 0 | 676.5459 | 6088.9132 | Aggreko | 13999170 | 12906917.2727 | 141976090 | 410 | 1922.7273 | 21150
Diesel Generation(Emergency) | 2 | 1.6 | 16 | Diesel | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | TOTAL | 23621770 | 22574455.4545 | 248319010 | 97740 | 77337.2727 | 850710

## PR-Pag3
May - 2021
BOILERS/STM. TURBINES | SS | GAS TURBINE | SS | STX. EMERGENCY DIESEL | SS | OTHERS | SS
| Kwh |  | Kwh |  | Kwh |  | Kwh
SS10 Plant Aux. Trans 480V | 0 | Plant SS |  | Diesel | 0 | Station Service Shops | 0
SS10 Unit Aux.. Trans 480V | 0 | Unit 16 | 0 |  |  | Station Service Office | 0
|  | Unit 17 | 11400 |  |  | Fuel Tanks SS | 0
Unit 10 Total Station Power | 0 | Unit 19 | 28000 | TOTAL DIESEL | 0 | Switch Yard SS | 195200
|  | Unit 20 | 57030 |  |  | Richmond Sub SS | 700
|  | Aggreko | 410 |  |  | Midland Sub SS | 21760
SS11 Plant Aux. Trans 480V | 0 |  |  |  |  | TOTAL OTHERS | 217660
SS11 Unit Aux.. Trans 480V | 0 | Unit SS |  | WATER PLANTS | SS
|  | Unit 16 | 0 |  | Kwh | SwitchGear Bkr1 SS | 1291947
Unit 11 Net Total Station Power | 0 | Unit 17 | 900 | Plant ABC Pump usage | 0 | SwitchGear Bkr3 SS | 382096
|  | Unit 19 | 0 |  |  | SS10 Unit Aux Trans. | 0
|  | Unit 20 | 0 | Intake Pump A&B+Chloropac | 0 | SS11 Unit Aux Trans. | 0
HRSG 21 Station Power | 0 | TOTAL GAS TURBINES | 97740 |  |  | Total GT Unit SS | 900
HRSG 24 Station Power** | 0 | Plant Pumps |  | RO Plant Electrical Usage | 533093
|  | Intake Pump A | 0 | UPW Electrical Usage | 13209.76 |  | 1674943
|  | Intake Pump B | 0 | RO ANNEX Electrical Usage | 708104
WHB Net Station Power | 0 | Intake Pump C | 0
TOTAL BOILERS / STM TURBINES | 0 |  |  | TOTAL WATER PLANTS | 1254406.76 | Total Station Service* | 1569806.76
*Total SS switched to a summaton of individual meters from general 'main' distribution meters summation
** No power to meter

## PR-Pag4
May - 2021
Desalination Plants Summary
|  | FYTD | TOTAL | Units Water Output
| Service | AVG. | FYTD | This Month | FYTD
Unit | HRS | HRS | HRS | GALS | GALS
RO 1 |  |  |  | 44259500 | 428537000
RO 2 |  |  |  | 60028333.3333 | 587731000
STX TOTALS |  |  |  | 104287833.3333 | 1016268000
Boilers Summary
|  | Boilers Service Hours |  |  | Make Up Feed Water |  | Low Pressure Steam |  | High Pressure Steam
| Service | AVG. | FYTD | This Month | AVG. | FYTD | This Month | FYTD | This Month | FYTD
Unit | HRS | HRS | HRS | GALS | GALS | GALS | LBS | AVG. | LBS | AVG.
HRSG 21/IPOS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HRSG 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Boiler 11 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
TOTALS |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Distribution |  | This Month | FYTD-AVG. | FYTD |  | Steam Summary |  | LP Steam | HP Steam
|  | GALS | GALS | GALS |  | ITEM |  | LBS | LBS
Total Plant Water Produced |  | 104287833.3333 | 92388000 | 1016268000 |  | Total Steam Produced |  | 0 | 0
Total Reverse Osmosis Produced |  | 104287833.3333 | 38957909.0909 | 428537000 |  | To Steam Turbine 10 |  |  | 0
Total to Distribution Tank |  | 102657288.6667 | 90756735.2727 | 998324088 |  | To Steam Turbine 11 |  |  | 0
Apparent Station Use |  | 1630544.6667 | 1631264.7273 | 17943912 |  | From Steam Turbine 10 |  | 0 | 0
Water to day Tank |  | 1101666.6667 | 1098393.9394 | 12082333.3333 |  | From Steam Turbine 11 |  | 0
UPW Feed |  | 1578244.6667 | 1598610.1818 | 17584712
UPW Product |  | 1101666.6667 | 1098393.9394 | 12082333.3333 |  | Used Steam for Production |  | 0 | 0
Water to the Demineralizer (Regen) |  | 0 | 0 | 0 |  | Others uses & Deareator |  |  | 0
Boilers Make Up |  | 0 | 0 | 0
Unit 16 Noxwater |  | 0 | 0 | 0
Unit 17 Noxwater |  | 433990.3564 | 1229279.824 | 13522078.064
Unit 19 Noxwater |  | 58103.653 | 101740.1137 | 1119141.2506
Unit 20 Noxwater |  | 297700.6836 | 370838.8672 | 2225033.2031
Metered Total Wtr to NOX |  | 1001600 | 973200 | 10705200
Station Wtr Warehouse & Eng. |  | 0 | 0 | 0
Plant Service Water |  | 52300 | 32654.5455 | 359200
Admin. Off. Water |  | 0 | 0 | 0
WTR to Fire Hydrants |  | 0 | 0 | 0 |  | * Unaccountable value has been zeroed due to non-functional distribution
Total Water used |  | 1630544.6667 | 1631264.7273 | 17943912 |  |  | meter giving rise to high unaccountable value
Unaccountable Water |  | 0 | 0 | 0

## PR-Pag5
May - 2021
| Feeders Power Distribution |  | This Month Total Plant Outages |  |  | Month | FYTD | FYTD | Feeders Outages Summary
| Output | FYTD | Planned | Forced | Time Hrs | Lost Sales | Total | Total | Feeder | Time | Date | Reason
Feeder | KWH | AVG KWH | Outages | Outages | Duration | Kwh | Outages | Time Hrs |  | min.
[9 empty] | Feeder #1A | 25 | 2021-05-07 | VTTI signal pull station, local fire call point varporization area
Feeder #1A (13Kv) | 1364094.13 | 1228735.6136 | 0 | 1 | 0.41667 | 764.3697 | 8 | 11.7833 | Feeder #2A | 26 | 2021-05-07 | VTTI signal pull station, local fire call point varporization area
Feeder #2A (13 Kv) | 2845663.94 | 2763975.2955 | 0 | 5 | 0.61667 | 2360.5938 | 44 | 35.6 | Feeder #3A | 51 | 2021-05-07 | VTTI signal pull station, local fire call point varporization area
Feeder #3A (13(Kv) | 1430000 | 1080675.1818 | 0 | 2 | 0.96667 | 1860.3921 | 25 | 17.9833 | Feeder #4A | 52 | 2021-05-07 | VTTI signal pull station, local fire call point varporization area
Feeder #4A (13 Kv) | 1432390.5 | 1397632.0227 | 0 | 3 | 0.98333 | 1895.6739 | 22 | 19.55 | Feeder #5A | 25 | 2021-05-07 | VTTI signal pull station, local fire call point varporization area
Feeder #5A (13 Kv) | 2850000 | 3320909.0909 | 0 | 1 | 0.41667 | 1596.9965 | 4 | 5.0167 | Feeder #6A | 52 | 2021-05-07 | VTTI signal pull station, local fire call point varporization area
Feeder #6A (13 Kv) | 1790051 | 1955461.4545 | 0 | 2 | 1 | 2409.2207 | 12 | 17.4333 | Feeder #8B | 25 | 2021-05-07 | VTTI signal pull station, local fire call point varporization area
Feeder #9A (13 Kv) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Feeder #9B | 51 | 2021-05-07 | VTTI signal pull station, local fire call point varporization area
Feeder #6B (24 Kv) | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 6.8667 | Feeder #10A | 27 | 2021-05-07 | VTTI signal pull station, local fire call point varporization area
Feeder #8B (24 Kv) | 4685118.5 | 5151248.7273 | 0 | 1 | 0.41667 | 2625.3046 | 8 | 6.8667 | Feeder #10B | 55 | 2021-05-07 | VTTI signal pull station, local fire call point varporization area
Feeder #9B(24Kv) | 2049093 | 2126094.8801 | 0 | 1 | 0.85 | 2343.7113 | 8 | 13.6667 | Feeder #2A | 3 | 2021-05-08 | Unit 20 tripped due to safety shutoff valve position fault
Feeder #10A(24Kv) | 1927327 | 1706804.4 | 0 | 0 | 0 | 0 | 0 | 0 | Feeder #3A | 7 | 2021-05-08 | Unit 20 tripped due to safety shutoff valve position fault
Feeder #10B(24Kv) | 1439499.125 | 1422569.2727 | 0 | 7 | 0.75 | 1452.5723 | 45 | 24.7833 | Feeder #4A | 6 | 2021-05-08 | Unit 20 tripped due to safety shutoff valve position fault
TOTALS | 21813237.195 | 22154105.9392 | 0 | 23 | 6.4167 | 17308.8349 | 184 | 159.55 | Feeder #6A | 8 | 2021-05-08 | Unit 20 tripped due to safety shutoff valve position fault
*Note Feeder 6A meter under invesigation. Value used is approximated | [8 empty] | Feeder #10A | 3 | 2021-05-08 | Unit 20 tripped due to safety shutoff valve position fault
[9 empty] | Feeder #2A | 4 | 2021-05-10 | Feeder opened due to insufficient load
[9 empty] | Feeder #10A | 3 | 2021-05-10 | Feeder opened due to insufficient load
[9 empty] | Feeder #2A | 2 | 2021-05-14 | Aggreko trip (G15 &G18)
[9 empty] | Feeder #10A | 3 | 2021-05-14 | Aggreko trip (G15 &G18)
[9 empty] | Feeder #2A | 2 | 2021-05-14 | Aggreko trip (G11)
[9 empty] | Feeder #10A | 4 | 2021-05-14 | Aggreko trip (G11)
[9 empty] | Feeder #10A | 4 | 2021-05-19 | Aggreko trip (G18)
[9 empty] | Feeder #10A | 1 | 2021-05-23 | Insufficient load due to solar swing
[9 empty] | Feeder #4A | 1 | 2021-05-31 | Feeder tripped due to insufficient load
0
0
0
0
0

## PR-Pag6
May - 2021
Power - Water Units Outages
|  | TOTAL NUMBER OF OUTAGES |  |  |  | PLANNED OUTAGES |  |  |  | FORCED OUTAGES
| This Month | FYTD | This Month | FYTD | This Month | FYTD | Duration | FYTD | This Month | FYTD | Duration | FYTD
Unit | Outages | Outages | Hours | Hours | Outages | Outages | Hours | Hours | Outages | Outages | Hours | Hours
Unit 10ST | 1 | 11 | 744 | 8040 | 1 | 11 | 744 | 8040 | 0 | 0 | 0 | 0
Unit 11ST | 1 | 11 | 744 | 8040 | 1 | 11 | 744 | 8040 | 0 | 0 | 0 | 0
Unit11BLR | 1 | 11 | 744 | 8040 | 1 | 11 | 744 | 8040 | 0 | 0 | 0 | 0
Unit 16 | 0 | 0 | 744 | 8040 | 0 | 0 | 744 | 8040 | 0 | 0 | 0 | 0
Unit 17 | 0 | 4 | 0 | 26.65 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 26.65
Unit 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Unit 20 | 1 | 11 | 0 | 4395.3167 | 1 | 11 | 0 | 4395.3167 | 0 | 0 | 0 | 0
Aggreko | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HRSG 21 | 1 | 11 | 744 | 8040 | 1 | 11 | 744 | 8040 | 0 | 0 | 0 | 0
HRSG 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTALS | 5 | 59 |  |  | 5 |  |  |  | 0 | 2
Plant Power Distribution
|  |  | This Month | FYTD | FYTD |  |  |  | Peak and Min. Load Data
|  |  | KWH | KWH | AVG. | [5 empty] | FYTD
Total 13KV Feeders |  |  | 11712199.57 | 129221275.25 | 11747388.6591 |  |  |  |  | This Month | AVG.
Total 24KV Feeders |  |  | 10101037.625 | 108514895.921 | 9864990.5383 |  |  | Peak Load (KW) |  | 38450 | 38669.0909
Feeder Totals |  |  | 21813237.195 | 237736171.171 | 21612379.1974 |  |  | Day |  | Tuesday
Total Generation |  |  | 24293725.5 | 255464167.25 | 23224015.2045 |  |  | Date |  | 2021-05-18
T1,T3,T4, T5, T6, T7 Available |  |  | 8962113 | 205432764 | 18675705.8182 |  |  | Hour |  | 19:12
T1&T3&T4&T5&T6&T7 Losses* |  |  | 804645.305 | 3755225.947 | 341384.177
Net Distributed |  |  | 23489080.195 | 251708941.303 | 22882631.0275 |  |  | Min. Load (KW) |  | 24970 | 24840.9091
Line Department |  |  |  | 0 | 0 |  |  | Day |  | Saturday
Water Department |  |  |  | 0 | 0 |  |  | Date |  | 2021-05-15
Power Plant Services |  |  |  | 0 | 0 |  |  | Hour |  | 6:00
Administration & General |  |  |  | 0 | 0
Plant Station Service |  |  |  | 0 | 0
Net Available from Bus |  |  |  | 0 | 0
Wapa KWH From Dist |  |  |  | 0 | 0 |  | * meters under review
SwitchGear Bkr1 SS |  |  | 1291947 | 12610173.5 | 1146379.4091
SwitchGear Bkr3 SS |  |  | 382096 | 3738306.25 | 339846.0227
Total Station Service Power |  |  | 1569806.76 | 16373319.75 | 1488483.6136
Net KWH Available for Sale |  |  | 21814137.195 | 235335621.553 | 21394147.4139
Plant Unaccountable |  |  | 0 | 0 | 0
0
0
0
0
0

## PR-Pag7
May - 2021
|  |  | Fuel Allocation | BBLS
|  |  | Propane Fuel For Power | 84687.9762
|  |  | Propane Fuel For Water | 0
|  |  | No 2 Fuel For Power | 2344.0406
|  |  | No 2 Fuel For Water | 0
|  |  | O&M Factor for Water | 0
Power Boilers
11
TPBSFC
BLR11FUELCOST
0 |  | GT Fuel Allocation
HP Stm from WHB
GTFCAE
WHBHPSTMCOST
Combined Cycle |  | 0
WHB, 16. 17. 20
TGTFC |  |  |  |  | Electrc Power
GEN1617FUELCOST |  |  |  |  | Generation
2298213.7497 |  |  |  |  | TOTFUELCOSTPWR
|  |  | Gas Turbine |  | 4235553.1644
Power Allocation
Simple Cycle |  |  | GTFCA
GEN161720ADJFCOST
GEN 19 FUELCOST |  |  | 2298213.7497
129228.7298
RO Water
DIESEL |  |  |  |  | Production Cost
Emergency Gen.
DIESEL_EMER. |  |  |  |  | 234898.1807
0
Cost Calculated at:
| 71.0774 | per BBL for No. 2
| 50.82 | per BBL for Propane

## PR-Pag8
May - 2021
Fuel Allocations
Fuel Summary |  |  |  | ITEM | Amount | FYTD
ITEM | Propane | No2 BBLS
|  |  |  | Electric Power Generation | 4235553.1644 | 41534406.3047
Inventory-Beginning of Month |  | 19559.2938 |  | Water Production* | 234898.1807 | 2144555.3166
Received During Month |  | 0 |  | Total #2 Fuel Cost | 166608.3951 | 4707342.4398
Consumed During Month |  | 2344.0406 |  | BBLS Propane for Power | 84687.9762 | 867753.3333
Inventory-End of Month |  | 17215.2533 |  | BBLS Propane for Water | 0 | 0
Calorific Value (BTU/GAL) | 91415 | 137924.0668 |  | BBLS No. 2 for Power | 2344.0406 | 66764.9496
|  |  |  | BBLS No.2 for Water | 0 | 0
|  |  |  | Propane BBL Cost | 50.82
End of Month- Fuel in Tanks |  |  |  | No. 2 BBL Cost | 71.0774
|  | No 2 BBLS |  | * Note: Includes RO Electric Usage
|  |  |  | No. 2 Oil Used | This Month | FYTD
Tank 1 |  | 0 |  | No. 2 Units | BBLS No. 2 | BBLS No. 2
Tank 2 |  | 0
Tank 3 |  | 4457.52 |  | Unit 11 | 0 | 0
Tank 4 |  | 4236.31 |  | Unit 16 | 0 | 0
Tank 5 |  | 4334.54 |  | Unit 17 | 380.8956 | 18814.5473
Tank 6 |  | 4186.88 |  | Unit 19 | 1818.14 | 35978.361
Tank 7 |  |  |  | Unit 20 | 145.005 | 11972.0413
TOTALS | 0 | 17215.2533 |  | Diesel Emergency | 0 | 0
|  |  |  | Total No. 2 Consumed | 2344.0406 | 66764.9496
Fuel Shipments |  |  |  | Propane Used | This Month | FYTD
|  | No2 | No2 | Propane Units | Gals | Gals
|  | Date | BBLS | Unit 16 | 0 | 0
|  |  |  | Unit 17 | 936478.9135 | 13507337.491
|  |  |  | Unit 20 | 931979.0075 | 5852113.4638
|  |  |  | Aggreko | 1688437.079 | 17086189.0452
|  |  |  | Total Propane Consumed | 3556895 | 36445640
TOTAL SHIPMENTS |  |  | 0
|  |  |  | Tank Fuel / Metered Fuel | Ratio
Used Oil recovered | 0 | Bbls
|  |  |  | No. 2 | 0.9727
|  |  |  | Propane | 0.94248
Ratio 0.95 to 1.05 acceptable
0
0
0
0
0

## PR-Pag9
May - 2021

## PR-Pag10
May - 2021

## PR-Pag11
May - 2021