## DataBase
FISCAL YEAR 2020-2021
|  | 31 | 31 | 30 | 31 | 30 | 31 | 31 | 28 | 31 | 30 | 31 | 0
|  | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY | JUN | FYTD | FYTD-AVG
Item | Index | 7 | 8 | 9 | 10 | 12 | 12 | 13 | 14 | 15 | 16 | 17 | 18
Total System Generation |  | 7: 25719.9895; 8: 25797.0635 | 51517.053 | 25758.5265
Gross Power Generation |  | 7: 25075.95; 8: 25132.08 | 50208.03 | 25104.015
Gross Water Production |  | 7: 90987.3333; 8: 89121.8333 | 180109.1667 | 90054.5833
System Load Factor |  | 7: 82.05%; 8: 80.83% | 162.9% | 81.44%
Total No. 6 Fuel Cost |  | 7: 0; 8: 0 | 0 | 0
Total No. 2 Fuel Cost |  | 7: 426605.2954; 8: 713645.361 | 1140250.6564 | 570125.3282
Total Propane Cost |  | 7: 3453706.8756; 8: 3267490.988 | 6721197.8636 | 3360598.9318
Power Fuel Cost (Internal) |  | 7: 0.15474; 8: 0.15841 | 0.31315 | 0.15658
Power Fuel Cost (to bus) |  | 7: 0.16018; 8: 0.16575 | 0.32594 | 0.16297
Water Fuel Cost (Internal) |  | 7: 1.8354; 8: 1.8579 | 3.6933 | 1.8466
Water Fuel Cost (to Distribution |  | 7: 1.872; 8: 1.8973 | 3.7693 | 1.8847
Total Power Fuel Cost |  | 7: 3713314.5045; 8: 3815559.4954 | 7528873.9999 | 3764437
Total Water Fuel Cost |  | 7: 166997.6665; 8: 165576.8536 | 332574.5201 | 166287.26
No. 6 Fuel Consumed |  | 7: 0; 8: 0 | 0 | 0
No. 2 Fuel Consumed |  | 7: 5520.1249; 8: 9234.3241 | 14754.449 | 7377.2245
No. 6 Fuel Received |  | 7: 0; 8: 0 | 0 | 0
No. 2 Fuel Received |  | 7: 0; 8: 32182.12 | 32182.12 | 32182.12
EOM No. 6 Fuel On Hand |  | 7: 0; 8: 0 | 0 | 0
EOM No. 2 Fuel On Hand(based on 2000Bbl/day Consumption) |  | 7: 17.1102; 8: 28.5841 | 45.6943 | 22.8472
Plant Water Use ( Internal) |  | 7: 15419.311; 8: 1941.8664 | 17361.1773 | 8680.5887
Plant Power Use (Internal) |  | 7: 276393.5654; 8: 281664.3417 | 558057.907 | 279028.9535
Heat Rates BTU/KWH | [13 empty] | 0 | 0
(Net Energy in KWH Produced) | [13 empty] | 0 | 0
Units | [13 empty] | 0 | 0
Combined Cycle-Units 10,16 |  | 7: 0; 8: 0 | 0 | 0
Combined Cycle-Units 11,16 |  | 7: 0; 8: 0 | 0 | 0
Unit 10-Steam (10 MW) |  | 7: N/A; 8: N/A | 0 | 0
Unit 11-Steam (21 MW) |  | 7: N/A; 8: N/A | 0 | 0
Unit 16-Gas Turbine (23 MW) |  | 7: 0; 8: 0 | 0 | 0
Unit 17-Gas Turbine (20.3 MW) |  | 7: 19723.3655; 8: 19377.4218 | 39100.7873 | 19550.3937
Unit 19-Gas Turbine (24 MW) |  | 7: 31163.4711; 8: 25705.1735 | 56868.6446 | 28434.3223
Unit 20_Gas Turbine (24 MW) |  | 7: 0; 8: 0 | 0 | 0
Aggreko |  | 7: 10887.2856; 8: 10962.7384 | 21850.024 | 10925.012
Total Plant . |  | 7: 15100.2454; 8: 15206.0874 | 30306.3328 | 15153.1664
Desal Performance Ratios | [13 empty] | 0 | 0
IDE3 (1.25MGD) |  | 7: 0; 8: 0 | 0 | 0
IDE4 (.55MGD) |  | 7: 0; 8: 0 | 0 | 0
IDE5 (0.55MGD) |  | 7: 0; 8: 0 | 0 | 0
IDE9 (1.3MGD) |  | 7: 0; 8: 0 | 0 | 0
Unit Availability Percent | [13 empty] | 0 | 0
Unit 10 | [13 empty] | 0% | 0% | bar: 7 to 8
Unit 11 | [13 empty] | 0% | 0% | bar: 7 to 8
Unit 16 | [13 empty] | 0% | 0% | bar: 7 to 8
Unit 17 |  | 7: 100%; 8: 100% | 200% | 100%
Unit 19 |  | 7: 100%; 8: 100% | 200% | 100%
Unit 20 | [13 empty] | 0% | 0% | bar: 7 to 8
Aggreko |  | 7: 100%; 8: 100% | 200% | 100%
IDE 3 |  | 7: 100%; 8: 100% | 200% | 100%
IDE 4 | [13 empty] | 0% | 0% | bar: 7 to 8
IDE 5 | [13 empty] | 0% | 0% | bar: 7 to 8
IDE 9 |  | 7: 100%; 8: 100% | 200% | 100%
HRSG 21 | [13 empty] | 0% | 0% | bar: 7 to 8
HRSG 24 |  | 7: 100%; 8: 100% | 200% | 100%
Pag2 | [13 empty] | 0 | 0
Item | [13 empty] | 0 | 0
Steam Turbine Generation |  | 7: 0; 8: 0 | 0 | 0
Gas Turbine Generation |  | 7: 25075950; 8: 25132080 | 50208030 | 25104015
Diesel Generation |  | 7: 0; 8: 0 | 0 | 0
Total Generation |  | 7: 25075950; 8: 25132080 | 50208030 | 25104015
IPP1 |  | 7: 644039.5; 8: 664983.5 | 1309023 | 654511.5
Total System Generation |  | 7: 25719989.5; 8: 25797063.5
Steam Station Power |  | 7: 0; 8: 0 | 0 | 0
Gas Turbine Station Power |  | 7: 45390; 8: 45350 | 90740 | 45370
Total Gen. Plant Station Power |  | 7: 45390; 8: 45350 | 90740 | 45370
Total Service / Gross Output |  | 7: 0.181%; 8: 0.1804% | 0.3615% | 0.1807%
Operating Hours | [13 empty] | 0 | 0
Unit 10 |  | 7: 0; 8: 0 | 0 | 0
Unit 11 |  | 7: 0; 8: 0 | 0 | 0
Unit 16 |  | 7: 0; 8: 0 | 0 | 0
Unit 17 |  | 7: 739.5; 8: 722.8 | 1462.3 | 731.15
Unit 19 |  | 7: 180.1; 8: 242.4 | 422.5 | 211.25
Unit 20 |  | 7: 0; 8: 0 | 0 | 0
Aggreko |  | 7: 713.003; 8: 697.0245 | 1410.0275 | 705.0138
Diesel Generation(Emergency) |  | 7: 1; 8: 3 | 4 | 2
Unit Average Loading | [13 empty] | 0 | 0
(KWH / Operating Hours) | [13 empty] | 0 | 0
Unit 10 |  | 7: 0; 8: 0 | 0 | 0
Unit 11 |  | 7: 0; 8: 0 | 0 | 0
Unit 16 |  | 7: 0; 8: 0 | 0 | 0
Unit 17 |  | 7: 13623.1508; 8: 13655.7831 | 27278.9338 | 13639.4669
Unit 19 |  | 7: 4553.0261; 8: 6600.6601 | 11153.6862 | 5576.8431
Unit 20 |  | 7: 0; 8: 0 | 0 | 0
Aggreko |  | 7: 19890; 8: 19600 | 39490 | 19745
Diesel |  | 7: 0; 8: 0 | 0 | 0
Utilization Factor | [13 empty] | 0 | 0
Unit 10 | [13 empty] | 0% | 0% | bar: 7 to 8
Unit 11 | [13 empty] | 0% | 0% | bar: 7 to 8
Unit 16 | [13 empty] | 0% | 0% | bar: 7 to 8
Unit 17 |  | 7: 62.21%; 8: 62.36% | 124.6% | 62.28%
Unit 19 |  | 7: 18.58%; 8: 26.94% | 45.53% | 22.76%
Unit 20 | [13 empty] | 0% | 0% | bar: 7 to 8
Aggreko |  | 7: 99.45%; 8: 98%
Diesel | 1 | [12 empty] | 0% | 0% | bar: 7 to 8
Unit Output KW | 2 | [12 empty] | 0 | 0
Unit 10 | 3 | 7: 0; 8: 0 | 0 | 0
Unit 11 | 4 | 7: 0; 8: 0 | 0 | 0
Unit 16 | 5 | 7: 0; 8: 0 | 0 | 0
Unit 17 | 6 | 7: 10074320; 8: 9870400 | 19944720 | 9972360
Unit 19 | 7 | 7: 820000; 8: 1600000 | 2420000 | 1210000
Unit 20 | 8 | 7: 0; 8: 0 | 0 | 0
Aggreko |  | 7: 14181630; 8: 13661680 | 27843310 | 13921655
Diesel |  | 7: 0; 8: 0 | 0 | 0
TOTAL | 9 | 7: 25075950; 8: 25132080 | 50208030 | 25104015
Unit Station Service Power | [13 empty] | 0 | 0
Unit 10 |  | 7: 0; 8: 0 | 0 | 0
Unit 11 |  | 7: 0; 8: 0 | 0 | 0
Unit 16 |  | 7: 0; 8: 0 | 0 | 0
Unit 17 |  | 7: 2370; 8: 3560 | 5930 | 2965
Unit 19 |  | 7: 35520; 8: 34800 | 70320 | 35160
Unit 20 |  | 7: 7500; 8: 6990 | 14490 | 7245
Aggreko |  | 7: 260; 8: 200 | 460 | 230
Diesel |  | 7: 0; 8: 0 | 0 | 0
TOTAL |  | 7: 45390; 8: 45350 | 90740 | 45370
pag3 | [13 empty] | 0 | 0
BOILERS/STM. TURBINES | [13 empty] | 0 | 0
[14 empty] | 0 | 0
SS10 Plant Aux. Trans 480V |  | 7: 0; 8: 0 | 0 | 0
SS10 Unit Aux.. Trans 480V |  | 7: 0; 8: 0 | 0 | 0
[14 empty] | 0 | 0
Unit 10 Total Station Power |  | 7: 0; 8: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
SS11 Plant Aux. Trans 480V |  | 7: 0; 8: 0 | 0 | 0
SS11 Unit Aux.. Trans 480V |  | 7: 0; 8: 0 | 0 | 0
[14 empty] | 0 | 0
Unit 11 Net Total Station Power |  | 7: 0; 8: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
HRSG 21 Station Power |  | 7: 0; 8: 0 | 0 | 0
HRSG 24 Station Power |  | 7: 0; 8: 0 | 0 | 0
WHB Net Station Power |  | 7: 0; 8: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
TOTAL BOILERS / STM TURBINES |  | 7: 0; 8: 0 | 0 | 0
GAS TURBINE | [13 empty] | 0 | 0
[14 empty] | 0 | 0
Plant SS | [13 empty] | 0 | 0
Unit 16 |  | 7: 0; 8: 0 | 0 | 0
Unit 17 |  | 7: 30; 8: 980 | 1010 | 505
Unit 19 |  | 7: 35520; 8: 34800 | 70320 | 35160
Unit 20 |  | 7: 0; 8: 5490 | 5490 | 5490
|  | 7: 260; 8: 200 | 460 | 230
Unit SS | [13 empty] | 0 | 0
Unit 16 |  | 7: 0; 8: 0 | 0 | 0
Unit 17 |  | 7: 2340; 8: 2580 | 4920 | 2460
Unit 19 |  | 7: 0; 8: 0 | 0 | 0
Unit 20 |  | 7: 7500; 8: 1500 | 9000 | 4500
|  | 7: 9840; 8: 4080 | 13920 | 6960
Plant IDE pumpage | [13 empty] | 0 | 0
IDE 4 |  | 7: 0; 8: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0 | 0 | 0
[14 empty] | 0 | 0
Total |  | 7: 0; 8: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
TOTAL GAS TURBINES |  | 7: 45650; 8: 45550 | 91200 | 45600
STX. EMERGENCY DIESEL | [13 empty] | 0 | 0
[14 empty] | 0 | 0
Diesel |  | 7: 0; 8: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
TOTAL DIESEL |  | 7: 0; 8: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
WATER PLANTS | [13 empty] | 0 | 0
[14 empty] | 0 | 0
IDE 3 |  | 7: 0; 8: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
IDE 9 |  | 7: 0; 8: 0 | 0 | 0
Intake Pump A |  | 7: 0; 8: 0 | 0 | 0
Intake Pump B |  | 7: 0; 8: 0 | 0 | 0
Intake Pump C |  | 7: 0; 8: 0 | 0 | 0
IDE Intake Pumps A&B+Chloropac |  | 7: 0; 8: 0 | 0 | 0
RO Plant |  | 7: 458594; 8: 477312 | 935906 | 467953
UPW Electricity |  | 7: 17911; 8: 17174 | 35085 | 17542.5
RO ANNEX Electricity |  | 7: 620604; 8: 567940 | 1188544 | 594272
TOTAL WATER PLANTS |  | 7: 1097109; 8: 1062426 | 2159535 | 1079767.5
OTHERS | [13 empty] | 0 | 0
[14 empty] | 0 | 0
Station Service Shops |  | 7: 25440; 8: 31680 | 57120 | 28560
Station Service Office | [13 empty] | 0 | 0
Fuel Tanks SS | [13 empty] | 0 | 0
Switch Yard SS |  | 7: 159360; 8: 161120 | 320480 | 160240
[14 empty] | 0 | 0
[14 empty] | 0 | 0
TOTAL OTHERS |  | 7: 184800; 8: 192800 | 377600 | 188800
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
SwitchGear Bkr1 SS |  | 7: 1126712.5; 8: 1097708.5 | 2224421 | 1112210.5
SwitchGear Bkr3 SS |  | 7: 301288.25; 8: 306636 | 607924.25 | 303962.125
[14 empty] | 0 | 0
Total |  | 7: 1428000.75; 8: 1404344.5 | 2832345.25 | 1416172.625
Total SS from GAC |  | 7: 9840; 8: 4080 | 13920 | 6960
Total Station Service Power |  | 7: 1327559; 8: 1300776 | 2628335 | 1314167.5
Total Unit #11 SS (Not Plant) | [13 empty] | 0 | 0
Total Unit #10 SS (Not Plant) | [13 empty] | 0 | 0
[14 empty] | 0 | 0
TOTAL STATION POWER |  | 7: 1786153; 8: 1778088 | 3564241 | 1782120.5
KWH | [13 empty] | 0
ENERGY DISTRIBUTION | [13 empty] | 0
0
0
0
0
GROSS ENERGY DISTRIBUTION | [13 empty] | 0
Gross Electric Energy Produced |  | 7: 0; 8: 0 | 0
Gross Energy Used in Water Plants |  | 7: 0; 8: 0 | 0
PLANT TOTAL GROSS ENERGY USED |  | 7: 0; 8: 0 | 0
0
NET ENERGY DISTRIBUTION | [13 empty] | 0
Net Electricity to Distribution |  | 7: 0; 8: 0 | 0
Net Energy used on water to distribution |  | 7: 0; 8: 0 | 0
PLANT TOTAL NET ENERGY USED |  | 7: 0; 8: 0 | 0
0
Plant Service / Gross Output |  | 7: 0; 8: 0 | 0
0
BTU's | [13 empty] | 0
Fuel No. 2 Consumed (BTU's) |  | 7: 0; 8: 0 | 0
Fuel No. 6 Consumed (BTU's) |  | 7: 0; 8: 0 | 0
TOTAL ENERGY IN FUEL |  | 7: 0; 8: 0 | 0
0
GROSS ENERGY DISTRIBUTION | [13 empty] | 0
Gross Electric Energy Produced |  | 7: 0; 8: 0 | 0
Gross Energy Used in Water Plants |  | 7: 0; 8: 0 | 0
PLANT TOTAL GROSS ENERGY USED |  | 7: 0; 8: 0 | 0
0
NET ENERGY DISTRIBUTION | [13 empty] | 0
Net Electricity to Distribution |  | 7: 0; 8: 0 | 0
Net Energy used on water to distribution |  | 7: 0; 8: 0 | 0
PLANT TOTAL NET ENERGY USED |  | 7: 0; 8: 0 | 0
0
Plant Service / NET Output |  | 7: 0; 8: 0 | 0
0
EFFICIENCY | [13 empty] | 0
0
Gross Efficiency | [13 empty] | 0
Electric Generating Plant Only |  | 7: 0; 8: 0 | 0
Water Desalination Plant only |  | 7: 0; 8: 0 | 0
Combined Generating and Water Plant |  | 7: 0; 8: 0 | 0
0
Net Efficiency | [13 empty] | 0
Electric Generating Plant Only |  | 7: 0; 8: 0 | 0
Water Desalination Plant only |  | 7: 0; 8: 0 | 0
Combined Generating and Water Plant |  | 7: 0; 8: 0 | 0
0
Heat Rates BTU/KWH | [13 empty] | 0
0
Gross Heat Rate | [13 empty] | 0
Electric Generating Plant Only |  | 7: 0; 8: 0 | 0
Water Desalination Plant only |  | 7: 0; 8: 0 | 0
Combined Generating and Water Plant |  | 7: 0; 8: 0 | 0
0
Net Heat Rate | [13 empty] | 0
Electric Generating Plant Only |  | 7: 0; 8: 0 | 0
Water Desalination Plant only |  | 7: 0; 8: 0 | 0
Combined Generating and Water Plant |  | 7: 0; 8: 0 | 0
[14 empty] | 0 | 0
pag4 | [13 empty] | 0 | 0
Desalination Plants Summary | [13 empty] | 0 | 0
Unit Service HRS | [13 empty] | 0 | 0
IDE 3 |  | 7: 0; 8: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0 | 0 | 0
Unit Output GALS | [13 empty] | 0 | 0
IDE 3 |  | 7: 0; 8: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0 | 0 | 0
From TC |  | 7: 0; 8: 0 | 0 | 0
RO WAPA Meter |  | 7: 0; 8: 0 | 0 | 0
RO 7Seas water Meter 1 |  | 7: 37516000; 8: 39683000 | 77199000 | 38599500
RO 7Seas water Meter 2 |  | 7: 37390000; 8: 39542000 | 76932000 | 38466000
RO Meter Average |  | 7: 37453000; 8: 39612500 | 77065500 | 38532750
RO 7Seas ANNEXwater Meter 1 |  | 7: 53489000; 8: 49507000
RO 7Seas ANNEX water Meter 2 |  | 7: 53630000; 8: 49527000
RO 7Seas ANNEX water Meter 3 |  | 7: 53484000; 8: 49494000
RO Meter Average |  | 7: 53534333.3333; 8: 49509333.3333 | 103043666.6667 | 51521833.3333
STX TOTALS |  | 7: 90987333.3333; 8: 89121833.3333 | 180109166.6667 | 90054583.3333
Unit Cond LBS | [13 empty] | 0 | 0
IDE 3 |  | 7: 0; 8: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0 | 0 | 0
STX TOTALS |  | 7: 0; 8: 0 | 0 | 0
Unit LP Steam LBS | [13 empty] | 0 | 0
[14 empty] | 0 | 0
IDE 3 |  | 7: 0; 8: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0 | 0 | 0
STX TOTALS |  | 7: 0; 8: 0 | 0 | 0
Unit HP Steam LBS | [13 empty] | 0 | 0
IDE 3 |  | 7: 0; 8: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0 | 0 | 0
STT TOTALS |  | 7: 0; 8: 0 | 0 | 0
Unit Utilization Factor Percent | [13 empty] | 0% | 0%
IDE 3 | [13 empty] | 0% | 0% | bar: 7 to 8
IDE 4 | [13 empty] | 0% | 0% | bar: 7 to 8
IDE 5 | [13 empty] | 0% | 0% | bar: 7 to 8
IDE 9 |  | 7: 0; 8: 0 | 0% | 0%
Boilers Summary | [13 empty] | 0 | 0
Service Hrs | [13 empty] | 0 | 0
WHB 21 |  | 7: 0; 8: 0 | 0 | 0
HRSG 24 |  | 7: 0; 8: 0 | 0 | 0
Boiler 11 |  | 7: 0; 8: 0 | 0 | 0
This Month Gals | [13 empty] | 0 | 0
WHB 21 |  | 7: 0; 8: 0 | 0 | 0
HRSG 24 |  | 7: 0; 8: 0 | 0 | 0
Boiler 11 |  | 7: 0; 8: 0 | 0 | 0
TOTALS |  | 7: 0; 8: 0 | 0 | 0
This Month LP STM LBS | [13 empty] | 0 | 0
WHB 21 |  | 7: 0; 8: 0 | 0 | 0
HRSG 24 |  | 7: 0; 8: 0 | 0 | 0
Boiler 11 | [13 empty] | 0 | 0
TOTALS |  | 7: 0; 8: 0 | 0 | 0
This Month HP STM LBS | [13 empty] | 0 | 0
WHB 21 |  | 7: 0; 8: 0 | 0 | 0
HRSG 24 |  | 7: 0; 8: 0 | 0 | 0
|  | 0 | 0
Boiler 11 |  | 7: 0; 8: 0 | 0 | 0
TOTALS |  | 7: 0; 8: 0 | 0 | 0
Water Distribution | [13 empty] | 0 | 0
Total Water Produced |  | 7: 90987333.3333; 8: 89121833.3333 | 180109166.6667 | 90054583.3333
Total to Distribution Tank |  | 7: 89206406.6667; 8: 87271346.6667 | 176477753.3333 | 88238876.6667
Apparent Station Use |  | 7: 1780926.6667; 8: 1850486.6667 | 3631413.3333 | 1815706.6667
Water to day Tank (Booster) Plus UPW Product |  | 7: 1151333.3333; 8: 1244333.3333 | 2395666.6667 | 1197833.3333
Water to the Demineralizer(regen) |  | 7: 0; 8: 0 | 0 | 0
Boilers Make Up |  | 7: 0; 8: 0 | 0 | 0
Unit 16 Noxwater |  | 7: 0; 8: 0 | 0 | 0
Unit 17 Noxwater |  | 7: 8237911.2549; 8: 813283.4473 | 9051194.7021 | 4525597.3511
Unit 19 Noxwater |  | 7: 136276.123; 8: 214627.1973 | 350903.3203 | 175451.6602
Unit 20 Noxwater |  | 7: 0; 8: 0 | 0 | 0
Total Wtr to NOX |  | 7: 1007500; 8: 1094100 | 2101600 | 1050800
Station Wtr Warehouse & Eng. |  | 7: 0; 8: 0 | 0 | 0
Plant Service Water |  | 7: 26900; 8: 17300 | 44200 | 22100
Admin. Off. Water |  | 7: 0; 8: 0 | 0 | 0
WTR to Fire Hydrants |  | 7: 0; 8: 0 | 0 | 0
Total Water Used |  | 7: 1780926.6667; 8: 1850486.6667 | 3631413.3333 | 1815706.6667
Unaccountable Water |  | 7: 0; 8: 0 | 0 | 0
Steam Summary | [13 empty] | 0 | 0
LP Steam LBS | [13 empty] | 0 | 0
Total Steam Produced |  | 7: 0; 8: 0 | 0 | 0
From Steam Turbine 10 |  | 7: 0; 8: 0 | 0 | 0
From Steam Turbine 11 |  | 7: 0; 8: 0 | 0 | 0
[14 empty] | 0 | 0
HP STM to IDE's Ejectors | [13 empty] | 0 | 0
LP STM to IDE's Process |  | 7: 0; 8: 0 | 0 | 0
Used Steam for Production |  | 7: 0; 8: 0 | 0 | 0
[14 empty] | 0 | 0
Others uses & Deareator |  | 7: 0; 8: 0 | 0 | 0
HP Steam LBS | [13 empty] | 0 | 0
Total Steam Produced |  | 7: 0; 8: 0 | 0 | 0
To Steam Turbine 10 |  | 7: 0; 8: 0 | 0 | 0
To Steam Turbine 11 |  | 7: 0; 8: 0 | 0 | 0
From Steam Turbines |  | 7: 0; 8: 0 | 0 | 0
HP STM to IDE's Ejectors |  | 7: 0; 8: 0 | 0 | 0
LP STM to IDE's Process | [13 empty] | 0 | 0
Used Steam for Production |  | 7: 0; 8: 0 | 0 | 0
[14 empty] | 0 | 0
Others uses & Deareator |  | 7: 0; 8: 0 | 0 | 0
Boiler MUF from MUF Meters |  | 7: 0; 8: 0 | 0 | 0
Boiler MUF from Desal Unit HPSTM Meters |  | 7: 0; 8: 0 | 0 | 0
Boilers MUF per Desal Design Quantities |  | 7: 0; 8: 0 | 0 | 0
LPSTM to Desal/Condensate Return | [13 empty] | 0% | 0% | bar: 7 to 8
Boiler 10 MUF/HPSTM Generated | [13 empty] | 0% | 0%
Boiler 11 MUF/HPSTM Generated |  | 7: N/A; 8: N/A | 0% | 0%
WHB MUF / HP & LPSTM Generated |  | 7: N/A; 8: N/A | 0 | 0
[14 empty] | 0% | 0%
pag5 | [13 empty] | 0% | 0%
Feeder KWH | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 7: 1360494.62; 8: 1358974.88 | 2719469.5 | 1359734.75
Feeder # 2 (13 Kv) |  | 7: 3241831.56; 8: 3157129.75 | 6398961.31 | 3199480.655
Feeder # 3 (13(Kv) |  | 7: 1111674; 8: 1126770 | 2238444 | 1119222
Feeder # 4 (13 Kv) |  | 7: 1542316.75; 8: 1558387 | 3100703.75 | 1550351.875
Feeder # 5 (13 Kv) |  | 7: 3890000; 8: 3720000 | 7610000 | 3805000
Feeder # 6 (13 Kv) |  | 7: 2272777; 8: 2244390 | 4517167 | 2258583.5
Feeder # 9A (13 Kv) |  | 7: 0; 8: 0 | 0 | 0
Feeder # 6B (24 Kv) |  | 7: 0; 8: 0 | 0 | 0
Feeder # 8 (24 Kv) |  | 7: 4999139.5; 8: 5863816.5 | 10862956 | 5431478
Feeder # 9B (24Kv) |  | 7: 4274225.25; 8: 2607787.671 | 6882012.921 | 3441006.4605
Feeder # 10A (24 Kv) |  | 7: 0; 8: 832165 | 832165 | 832165
Feeder # 10 (24 Kv) |  | 7: 1532181; 8: 1548799.5 | 3080980.5 | 1540490.25
TOTALS |  | 7: 24224639.68; 8: 24018220.301 | 48242859.981 | 24121429.9905
Feeder Planned Outages | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 7: 0; 8: 0 | 0 | 0
Feeder # 2 (13 Kv) |  | 7: 0; 8: 0 | 0 | 0
Feeder # 3 (13(Kv) |  | 7: 0; 8: 0 | 0 | 0
Feeder # 4 (13 Kv) |  | 7: 0; 8: 0 | 0 | 0
Feeder # 5 (13 Kv) |  | 7: 0; 8: 0 | 0 | 0
Feeder # 6 (13 Kv) |  | 7: 0; 8: 0 | 0 | 0
Feeder # 6B (24 Kv) |  | 7: 0; 8: 0
Feeder # 8 (24 Kv) |  | 7: 0; 8: 0 | 0 | 0
Feeder # 9 (24Kv) |  | 7: 0; 8: 0 | 0 | 0
Feeder # 10 (24 Kv) |  | 7: 0; 8: 0 | 0 | 0
TOTALS |  | 7: 0; 8: 0 | 0 | 0
Feeder Forced Outages | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 7: 1; 8: 2 | 3 | 1.5
Feeder # 2 (13 Kv) |  | 7: 9; 8: 2 | 11 | 5.5
Feeder # 3 (13(Kv) |  | 7: 1; 8: 3 | 4 | 2
Feeder # 4 (13 Kv) |  | 7: 1; 8: 3 | 4 | 2
Feeder # 5 (13 Kv) |  | 7: 1; 8: 2 | 3 | 1.5
Feeder # 6 (13 Kv) | [13 empty] | 2 | 1 | bar: 7 to 8
Feeder # 6B (24 Kv) |  | 7: 0; 8: 0
Feeder # 8 (24 Kv) |  | 7: 4; 8: 1 | 5 | 2.5
Feeder # 9 (24Kv) |  | 7: 2; 8: 1 | 3 | 1.5
Feeder # 10 (24 Kv) |  | 7: 0; 8: 4 | 4 | 4
TOTALS |  | 7: 20; 8: 19 | 39 | 19.5
Feeder Total Outages HRS | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 7: 0.41667; 8: 2.25 | 2.6667 | 1.3333
Feeder # 2 (13 Kv) |  | 7: 1.75; 8: 15.9167 | 17.6667 | 8.8333
Feeder # 3 (13(Kv) |  | 7: 0.43333; 8: 4.35 | 4.7833 | 2.3917
Feeder # 4 (13 Kv) |  | 7: 0.81667; 8: 3.0167 | 3.8333 | 1.9167
Feeder # 5 (13 Kv) |  | 7: 0.41667; 8: 2.2333 | 2.65 | 1.325
Feeder # 6 (13 Kv) |  | 7: 0.83333; 8: 2.8167 | 3.65 | 1.825
Feeder # 6B (24 Kv) |  | 7: 0; 8: 0
Feeder # 8 (24 Kv) |  | 7: 1.3833; 8: 2.2833 | 3.6667 | 1.8333
Feeder # 9 (24Kv) |  | 7: 2.1; 8: 2.8333 | 4.9333 | 2.4667
Feeder # 10 (24 Kv) |  | 7: 0; 8: 6.5667 | 6.5667 | 6.5667
Feeder loss sales KWH | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 7: 762.3527; 8: 4122.2696 | 4884.6223 | 2442.3112
Feeder # 2 (13 Kv) |  | 7: 7643.2539; 8: 69018.1735 | 76661.4275 | 38330.7137
Feeder # 3 (13(Kv) |  | 7: 647.8577; 8: 6626.7147 | 7274.5724 | 3637.2862
Feeder # 4 (13 Kv) |  | 7: 1694.8156; 8: 6344.4532 | 8039.2688 | 4019.6344
Feeder # 5 (13 Kv) |  | 7: 2179.7602; 8: 11200.2876 | 13380.0478 | 6690.0239
Feeder # 6 (13 Kv) |  | 7: 2548.5277; 8: 8529.1968 | 11077.7245 | 5538.8622
Feeder # 6B (24 Kv) |  | 7: 0; 8: 0
Feeder # 8 (24 Kv) |  | 7: 9312.3096; 8: 18051.4316 | 27363.7412 | 13681.8706
Feeder # 9 (24Kv) |  | 7: 12098.4944; 8: 9969.0556 | 22067.5501 | 11033.775
Feeder # 10 (24 Kv) |  | 7: 0; 8: 13791.6875 | 13791.6875 | 13791.6875
TOTALS |  | 7: 36887.3718; 8: 147653.2701 | 184540.6419 | 92270.321
Plant Feeder Total Planned Outages | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 2 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 3 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 4 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 5 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 6 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 9 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 10 |  | 7: 0; 8: 0 | 0 | 0
TOTALS |  | 7: 0; 8: 0 | 0 | 0
Plant Feeder Total Forced Outages | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 0; 8: 2 | 2 | 2
Feeder # 2 |  | 7: 9; 8: 2 | 11 | 5.5
Feeder # 3 |  | 7: 0; 8: 3 | 3 | 3
Feeder # 4 |  | 7: 0; 8: 3 | 3 | 3
Feeder # 5 |  | 7: 0; 8: 2 | 2 | 2
Feeder # 6 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 4; 8: 0 | 4 | 4
Feeder # 9 |  | 7: 2; 8: 0 | 2 | 2
Feeder # 10 |  | 7: 0; 8: 4 | 4 | 4
TOTALS |  | 7: 15; 8: 16 | 31 | 15.5
Plant Feeder Total Outages Time | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 0.41667; 8: 2.25 | 2.6667 | 1.3333
Feeder # 2 |  | 7: 1.75; 8: 15.9167 | 17.6667 | 8.8333
Feeder # 3 |  | 7: 0.43333; 8: 4.35 | 4.7833 | 2.3917
Feeder # 4 |  | 7: 0.81667; 8: 3.0167 | 3.8333 | 1.9167
Feeder # 5 |  | 7: 0.41667; 8: 2.2333 | 2.65 | 1.325
Feeder # 6 |  | 7: 0.83333; 8: 2.8167 | 3.65 | 1.825
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 1.3833; 8: 2.2833 | 3.6667 | 1.8333
Feeder # 9 |  | 7: 2.1; 8: 2.8333 | 4.9333 | 2.4667
Feeder # 10 |  | 7: 0; 8: 6.5667 | 6.5667 | 6.5667
TOTALS | [13 empty] | 0 | 0
Plant Feeder Total Loss sales | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 762.3527; 8: 4122.2696 | 4884.6223 | 2442.3112
Feeder # 2 |  | 7: 7643.2539; 8: 69018.1735 | 76661.4275 | 38330.7137
Feeder # 3 |  | 7: 647.8577; 8: 6626.7147 | 7274.5724 | 3637.2862
Feeder # 4 |  | 7: 1694.8156; 8: 6344.4532 | 8039.2688 | 4019.6344
Feeder # 5 |  | 7: 2179.7602; 8: 11200.2876 | 13380.0478 | 6690.0239
Feeder # 6 |  | 7: 2548.5277; 8: 8529.1968 | 11077.7245 | 5538.8622
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 9312.3096; 8: 18051.4316 | 27363.7412 | 13681.8706
Feeder # 9 |  | 7: 12098.4944; 8: 9969.0556 | 22067.5501 | 11033.775
Feeder # 10 |  | 7: 0; 8: 13791.6875 | 13791.6875 | 13791.6875
TOTALS |  | 7: 36887.3718; 8: 147653.2701 | 184540.6419 | 92270.321
Line Feeder Total Planned Outages | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 2 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 3 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 4 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 5 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 6 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 9 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 10 |  | 7: 0; 8: 0 | 0 | 0
TOTALS |  | 7: 0; 8: 0 | 0 | 0
Line Feeder Total Forced Outages | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 1; 8: 0 | 1 | 1
Feeder # 2 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 3 |  | 7: 1; 8: 0 | 1 | 1
Feeder # 4 |  | 7: 1; 8: 0 | 1 | 1
Feeder # 5 |  | 7: 1; 8: 0 | 1 | 1
Feeder # 6 | [13 empty] | 2 | 1 | bar: 7 to 8
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 0; 8: 1 | 1 | 1
Feeder # 9 |  | 7: 0; 8: 1 | 1 | 1
Feeder # 10 |  | 7: 0; 8: 0 | 0 | 0
TOTALS |  | 7: 5; 8: 3 | 8 | 4
Line Feeder Total Outages Time | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 2 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 3 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 4 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 5 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 6 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 9 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 10 |  | 7: 0; 8: 0 | 0 | 0
TOTALS | [13 empty] | 0 | 0
Line Feeder Total Loss sales | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 2 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 3 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 4 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 5 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 6 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 9 |  | 7: 0; 8: 0 | 0 | 0
Feeder # 10 |  | 7: 0; 8: 0 | 0 | 0
TOTALS |  | 7: 0; 8: 0 | 0 | 0
pag6 | [13 empty] | 0 | 0
Units Outages | [13 empty] | 0 | 0
Unit 10 ST | [13 empty] | 2 | 1 | bar: 7 to 8
Unit 11 ST | [13 empty] | 2 | 1 | bar: 7 to 8
Unit 11 BLR | [13 empty] | 2 | 1 | bar: 7 to 8
Unit 16 |  | 7: 0; 8: 0 | 0 | 0
Unit 17 | [13 empty] | 2 | 1 | bar: 7 to 8
Unit 19 |  | 7: 0; 8: 0 | 0 | 0
Unit 20 | [13 empty] | 2 | 1 | bar: 7 to 8
Aggreko |  | 7: 0; 8: 0 | 0 | 0
IDE 3 |  | 7: 0; 8: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0 | 0 | 0
HRSG 21 | [13 empty] | 2 | 1 | bar: 7 to 8
HRSG 24 |  | 7: 0; 8: 0
Units Outages Duration | [13 empty] | 0 | 0
Unit 10 ST |  | 7: 744; 8: 744 | 1488 | 744
Unit 11 ST |  | 7: 744; 8: 744 | 1488 | 744
Unit 11 BLR |  | 7: 744; 8: 744 | 1488 | 744
Unit 16 |  | 7: 744; 8: 744 | 1488 | 744
Unit 17 |  | 7: 0; 8: 0 | 0 | 0
Unit 19 |  | 7: 0; 8: 0 | 0 | 0
Unit 20 |  | 7: 744; 8: 744 | 1488 | 744
Aggreko |  | 7: 0; 8: 0 | 0 | 0
IDE 3 |  | 7: 0; 8: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0 | 0 | 0
HRSG 21 |  | 7: 744; 8: 744 | 1488 | 744
HRSG 24 |  | 7: 0; 8: 0 | 0 | 0
Unit Planned Outages | [13 empty] | 0 | 0
Unit 10 ST | [13 empty] | 2 | 1 | bar: 7 to 8
Unit 11 ST | [13 empty] | 2 | 1 | bar: 7 to 8
Unit 11 BLR | [13 empty] | 2 | 1 | bar: 7 to 8
Unit 16 |  | 7: 0; 8: 0 | 0 | 0
Unit 17 | [13 empty] | 2 | 1 | bar: 7 to 8
Unit 19 |  | 7: 0; 8: 0 | 0 | 0
Unit 20 | [13 empty] | 2 | 1 | bar: 7 to 8
Aggreko |  | 7: 0; 8: 0 | 0 | 0
IDE 3 |  | 7: 0; 8: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0 | 0 | 0
HRSG 21 | [13 empty] | 2 | 1 | bar: 7 to 8
HRSG 24 |  | 7: 0; 8: 0
Unit Planned Outages Duration | [13 empty] | 0 | 0
Unit 10 ST |  | 7: 744; 8: 744 | 1488 | 744
Unit 11 ST |  | 7: 744; 8: 744 | 1488 | 744
Unit 11 BLR |  | 7: 744; 8: 744 | 1488 | 744
Unit 16 |  | 7: 744; 8: 744 | 1488 | 744
Unit 17 |  | 7: 0; 8: 0 | 0 | 0
Unit 19 |  | 7: 0; 8: 0 | 0 | 0
Unit 20 |  | 7: 744; 8: 744 | 1488 | 744
Aggreko |  | 7: 0; 8: 0 | 0 | 0
IDE 3 |  | 7: 0; 8: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0 | 0 | 0
HRSG 21 |  | 7: 744; 8: 744 | 1488 | 744
HRSG 24 |  | 7: 0; 8: 0
Unit Forced Outages |  | 7: 0; 8: 0 | 0 | 0
Unit 10 ST |  | 7: 0; 8: 0 | 0 | 0
Unit 11 ST |  | 7: 0; 8: 0 | 0 | 0
Unit 11 BLR |  | 7: 0; 8: 0 | 0 | 0
Unit 16 |  | 7: 0; 8: 0 | 0 | 0
Unit 17 |  | 7: 0; 8: 0 | 0 | 0
Unit 19 |  | 7: 0; 8: 0 | 0 | 0
Unit 20 |  | 7: 0; 8: 0 | 0 | 0
Aggreko |  | 7: 0; 8: 0 | 0 | 0
IDE 3 |  | 7: 0; 8: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0 | 0 | 0
HRSG 21 |  | 7: 0; 8: 0 | 0 | 0
HRSG 24 |  | 7: 0; 8: 0
Unit Forced Outages Duration |  | 7: 0; 8: 0 | 0 | 0
Unit 10 ST |  | 7: 0; 8: 0 | 0 | 0
Unit 11 ST |  | 7: 0; 8: 0 | 0 | 0
Unit 11 BLR |  | 7: 0; 8: 0 | 0 | 0
Unit 16 |  | 7: 0; 8: 0 | 0 | 0
Unit 17 |  | 7: 0; 8: 0 | 0 | 0
Unit 19 |  | 7: 0; 8: 0 | 0 | 0
Unit 20 |  | 7: 0; 8: 0 | 0 | 0
Aggreko |  | 7: 0; 8: 0 | 0 | 0
IDE 3 |  | 7: 0; 8: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0 | 0 | 0
HRSG 21 |  | 7: 0; 8: 0 | 0 | 0
HRSG 24 |  | 7: 0; 8: 0
Plant Power Distribution | [13 empty] | 0 | 0
Total 13KV Feeders |  | 7: 13419093.93; 8: 13165651.63 | 26584745.56 | 13292372.78
Total 24KV Feeders |  | 7: 10805545.75; 8: 10852568.671 | 21658114.421 | 10829057.2105
Feeder Totals |  | 7: 24224639.68; 8: 24018220.301 | 48242859.981 | 24121429.9905
Total Generation |  | 7: 25719989.5; 8: 25797063.5 | 51517053 | 25758526.5
24 KV BUS at XFMR-1 (T1) |  | 7: 66909.75; 8: 391221.84 | 458131.59 | 229065.795
24 KV BUS at XFMR-2 (T2) |  | 7: 0; 8: 0 | 0 | 0
24 KV BUS at XFMR-3 (T3) |  | 7: 0; 8: 0 | 0 | 0
XFMR T1 in |  | 7: 66510; 8: 389244
XFMR T1 out |  | 7: 4351087; 8: 4122766
XFMR T3 in |  | 7: 0; 8: 0
XFMR T3 out |  | 7: 0; 8: 0
XFMR T4in (from #16) |  | 7: 0; 8: 0
XFMR T4 out ( |  | 7: 0; 8: 0
XFMR T5 in (from #20) |  | 7: 0; 8: 99999416
XFMR T5 out |  | 7: 5558411; 8: 5172388
T1 &T3&T4 & T5 Available |  | 7: 9976008; 8: 109683814 | 119659822 | 59829911
T1 &T3 & T4 & T5 Losses |  | 7: 47669.07; 8: 366338.699 | 414007.769 | 207003.8845
Net Distributed |  | 7: 25672320.43; 8: 25430724.801 | 51103045.231 | 25551522.6155
Line Department |  | 7: 0; 8: 0 | 0 | 0
Water Department |  | 7: 0; 8: 0 | 0 | 0
Power Plant Services |  | 7: 0; 8: 0 | 0 | 0
Administration & General |  | 7: 0; 8: 0 | 0 | 0
Plant Station Service |  | 7: 0; 8: 0 | 0 | 0
Net Available from Bus |  | 7: 0; 8: 0 | 0 | 0
Wapa KWH From Dist |  | 7: 0; 8: 0 | 0 | 0
SwitchGear Bkr1 SS |  | 7: 1126712.5; 8: 1097708.5 | 2224421 | 1112210.5
SwitchGear Bkr3 SS |  | 7: 301288.25; 8: 306636 | 607924.25 | 303962.125
Total Station Service Power |  | 7: 1437840.75; 8: 1408424.5 | 2846265.25 | 1423132.625
Net KWH Available for Sale |  | 7: 24234479.68; 8: 24022300.301 | 48256779.981 | 24128389.9905
Plant Unaccountable |  | 7: 0; 8: 0
Peak Load: |  | 7: 41080; 8: 41790 | 82870 | 41435
Day |  | 7: Thursday; 8: Sunday |  | 0
Date |  | 7: 2020-07-02; 8: 2020-08-16
Hour |  | 7: 19:20; 8: 19:21
Min Load |  | 7: 27650; 8: 26320 | 53970 | 26985
Day |  | 7: Sunday; 8: Wednesday
Date |  | 7: 2020-07-19; 8: 2020-08-05
Hour |  | 7: 6:00; 8: 6:00 |  | 6:00
Pag 7
No 6 Fuel For Power |  | 7: 0; 8: 0 | 0 | 0
No 6 Fuel For Water |  | 7: 0; 8: 0 | 0 | 0
No 2 Fuel For Power |  | 7: 5520.1249; 8: 9234.3241 | 14754.449 | 7377.2245
No 2 Fuel For Water |  | 7: 0; 8: 0 | 0 | 0
O&M Factor for Water |  | 7: 0; 8: 0 | 0 | 0
BLR11FUEL2COST |  | 7: 0; 8: 0 | 0 | 0
Firing | [13 empty] | 0 | 0
WHBSFCAE |  | 7: 0; 8: 0 | 0 | 0
Power Boilers | [13 empty] | 0 | 0
[14 empty] | 0 | 0
TPBSFC | [13 empty] | 0 | 0
BLR11FUELCOST |  | 7: 0; 8: 0 | 0 | 0
Combined Cycle | [13 empty] | 0 | 0
WHB, 16 & 17 | [13 empty] | 0 | 0
TGTFC | [13 empty] | 0 | 0
GEN161720FUELCOST |  | 7: 1999545.5291; 8: 1941412.8559 | 3940958.385 | 1970479.1925
Simple Cycle | [13 empty] | 0 | 0
12 & 14 & 22 | [13 empty] | 0 | 0
GEN 19FUELCOST |  | 7: 343756.9591; 8: 552396.4641 | 896153.4232 | 448076.7116
DIESEL | [13 empty] | 0 | 0
7 St. John | [13 empty] | 0 | 0
DIESEL_EMER. |  | 7: 0; 8: 0 | 0 | 0
GT Fuel Allocation | [13 empty] | 0 | 0
HP Stm from WHB | [13 empty] | 0 | 0
GTFCAE | [13 empty] | 0 | 0
WHBHPSTMCOST |  | 7: 0; 8: 0 | 0 | 0
whb Benefit | [13 empty] | 0 | 0
Equalization to Water | [13 empty] | 0 | 0
WHBBECW | [13 empty] | 0 | 0
WHBBENCOSTWTR |  | 7: 0; 8: 0 | 0 | 0
Extraction Benefit | [13 empty] | 0 | 0
Equalization to Water | [13 empty] | 0 | 0
BECW | [13 empty] | 0 | 0
BENEQFCOSTWTR |  | 7: 0; 8: 0 | 0 | 0
Gas Turbine | [13 empty] | 0 | 0
Power Allocation | [13 empty] | 0 | 0
GTFCA | [13 empty] | 0 | 0
GEN161720ADJFCOST |  | 7: 1999545.5291; 8: 1941412.8559 | 3940958.385 | 1970479.1925
Extraction Incremental | [13 empty] | 0 | 0
to Water | [13 empty] | 0 | 0
FCAWI | [13 empty] | 0 | 0
INCRFUELCOSTWTR |  | 7: 0; 8: 0 | 0 | 0
GT Fuel Allocation | [13 empty] | 0 | 0
LP Stm from WHB | [13 empty] | 0 | 0
WHBFCAW | [13 empty] | 0 | 0
WHBLPSTMCOST |  | 7: 0; 8: 0 | 0 | 0
Electrc Power | [13 empty] | 0 | 0
Generation | [13 empty] | 0 | 0
TOTFUELCOSTPWR |  | 7: 3713314.5045; 8: 3815559.4954 | 7528873.9999 | 3764437
RO Electricity cost |  | 7: 70963.9268; 8: 75610.3018 | 146574.2286 | 73287.1143
UPW Electicity Cost |  | 7: 2771.5908; 8: 2720.5084 | 5492.0992 | 2746.0496
RO Annex Electricity cost |  | 7: 96033.7397; 8: 89966.5518
TOTFUELCSRWTR |  | 7: 166997.6665; 8: 165576.8536 | 332574.5201 | 166287.26
Pag8 | [13 empty] | 0 | 0
No 2 BBLS | [13 empty] | 0 | 0
Inventory-Beginning of Month |  | 7: 39740.5629; 8: 34220.4379 | 73961.0008 | 36980.5004
Received During Month |  | 7: 0; 8: 32182.12 | 32182.12 | 32182.12
Consumed During Month |  | 7: 5520.1249; 8: 9234.3241 | 14754.449 | 7377.2245
Inventory-End of Month |  | 7: 34220.4379; 8: 57168.2338 | 91388.6717 | 45694.3359
Calorific Value (BTU/GAL) |  | 7: 136784.2908; 8: 136999.0879 | 273783.3787 | 136891.6893
Calorific Value (BTU/GAL) |  | 7: 136784.2908; 8: 136999.0879 | 273783.3787 | 136891.6893
No 6 BBLS | [13 empty] | 0 | 0
Inventory-Beginning of Month |  | 7: 0; 8: 0 | 0 | 0
Received During Month |  | 7: 0; 8: 0 | 0 | 0
Consumed During Month |  | 7: 0; 8: 0 | 0 | 0
Inventory-End of Month |  | 7: 0; 8: 0 | 0 | 0
Calorific Value (BTU/GAL) |  | 7: 0; 8: 0 | 0 | 0
PROPANE
Propane Value (BTU/Gal) |  | 7: 91735; 8: 91735
End of Month- Fuel in Tanks | [13 empty] | 0 | 0
No 2 BBLS | [13 empty] | 0 | 0
Tank 1 #2 |  | 7: 0; 8: 0 | 0 | 0
Tank 2 #2 |  | 7: 0; 8: 0 | 0 | 0
Tank 5 #2 |  | 7: 8440.91; 8: 37021.4 | 45462.31 | 22731.155
Tank 6 #2 |  | 7: 17422.64; 8: 11760.45 | 29183.09 | 14591.545
TOTAL |  | 7: 34220.44; 8: 57168.23 | 91388.67 | 45694.335
No 6 BBLS | [13 empty] | 0 | 0
Tank 3 #2 |  | 7: 4452.57; 8: 4450.29 | 8902.86 | 4451.43
Tank 4 #6 |  | 7: 3904.33; 8: 3936.1 | 7840.43 | 3920.215
Tank 7 #6 |  | 7: 0; 8: 0 | 0 | 0
TOTAL |  | 7: 0; 8: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
Fuel Shipments | [13 empty] | 0 | 0
Date(1) |  | 7: 0; 8: 2020-08-19 | 2020-08-19 | 2020-08-19
No2 BBLS |  | 7: 0; 8: 32182.12 | 32182.12 | 32182.12
Date(2) |  | 7: 0; 8: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0 | 0 | 0
Date(3) |  | 7: 0; 8: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0 | 0 | 0
Date(4) |  | 7: 0; 8: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0 | 0 | 0
Date(5) |  | 7: 0; 8: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0 | 0 | 0
Date(6) |  | 7: 0; 8: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0 | 0 | 0
Date(7) |  | 7: 0; 8: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0 | 0 | 0
Date(8) |  | 7: 0; 8: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0 | 0 | 0
Date(9) |  | 7: 0; 8: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0 | 0 | 0
TOTAL SHIPMENTS No 2 |  | 7: 0; 8: 32182.12 | 32182.12 | 32182.12
Date(1) |  | 7: 0; 8: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0 | 0 | 0
Date(2) |  | 7: 0; 8: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0 | 0 | 0
Date(3) |  | 7: 0; 8: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0 | 0 | 0
Date(4) |  | 7: 0; 8: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0 | 0 | 0
Date(5) |  | 7: 0; 8: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0 | 0 | 0
Date(6) |  | 7: 0; 8: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0 | 0 | 0
Date(7) |  | 7: 0; 8: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0 | 0 | 0
Date(8) |  | 7: 0; 8: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0 | 0 | 0
TOTAL SHIPMENTS No 6 |  | 7: 0; 8: 0 | 0 | 0
[14 empty] | 0 | 0
Fuel Allocations Amount | [13 empty] | 0 | 0
Electric Power Generation |  | 7: 3713314.5045; 8: 3815559.4954 | 7528873.9999 | 3764437
Water Production |  | 7: 166997.6665; 8: 165576.8536 | 332574.5201 | 166287.26
Total #2 Fuel Cost |  | 7: 426605.2954; 8: 713645.361 | 1140250.6564 | 570125.3282
BBLS No. 6 for Power |  | 7: 0; 8: 0 | 0 | 0
BBLS No.6 for Water |  | 7: 0; 8: 0 | 0 | 0
BBLS No. 2 for Power |  | 7: 5520.1249; 8: 9234.3241 | 14754.449 | 7377.2245
BBLS No.2 for Water |  | 7: 0; 8: 0 | 0 | 0
No. 6 BBL Cost |  | 7: 71.9034; 8: 71.9034 | 143.8068 | 71.9034
No. 2 BBL Cost |  | 7: 77.2818; 8: 77.2818 | 154.5636 | 77.2818
Propane Cost per Bbl |  | 7: 38.3544; 8: 38.262
Propane Consumed
Unit 16 |  | 7: 0; 8: 0 | 0
Unit 17 |  | 7: 2098879.9746; 8: 1954076.7936 | 4052956.7682
Unit 20 |  | 7: 0; 8: 0 | 0 | 0
Aggreko |  | 7: 1683103.0254; 8: 1632631.2064 | 3315734.2318
No. 2 Units BBLS No. 2 Consumed | [13 empty] | 0 | 0
Unit 10 |  | 7: 0; 8: 0 | 0 | 0
Unit 11 |  | 7: 0; 8: 0 | 0 | 0
Unit 16 |  | 7: 0; 8: 0 | 0 | 0
Unit 17 |  | 7: 1072.0288; 8: 2086.5049 | 3158.5338 | 1579.2669
Unit 19 |  | 7: 4448.0961; 8: 7147.8192 | 11595.9153 | 5797.9576
Unit 20 |  | 7: 0; 8: 0 | 0 | 0
Diesel Emergency |  | 7: 0; 8: 0 | 0 | 0
Total No. 2 Consumed |  | 7: 5520.1249; 8: 9234.3241 | 14754.449 | 7377.2245
Note on I673: Nicholson: negative

## PR-Pag1
August - 2020
Production Summary |  |  |  |  | Generating Units Heat Rate |  | FYTD | This Month
|  | FYTD | FYTD |  | (Gross Energy in KWH Produced) | This Month | AVG. | %
Item | This Month | AVG. | TOTAL | Units | Units | BTU/KWH | BTU/KWH | Efficiency
Total System Gross Generation** | 25797.0635 | 25758.5265 | 51517.053 | MWH
Gross Power Plant Generation | 25132.08 | 25104.015 | 50208.03 | MWH
Gross Water Production | 89121.8333 | 90054.5833 | 180109.1667 | KGAL
System Load Factor | 80.83% | 81.44% |  | % | Unit 10-Steam (10 MW) + WHBs* | N/A | N/A | N/A
Total Propane Fuel Cost | 3267490.988 | 3360598.9318 | 6721197.8636 | $ | Unit 11-Steam (19.1 MW) + WHBs | N/A | N/A | N/A
Total No. 2 Fuel Cost | 713645.361 | 570125.3282 | 1140250.6564 | $ | Unit 16-Gas Turbine (22.5 MW) | 0 | 0 | 0%
Power Fuel Cost (Internal) | 0.15841 | 0.15658 |  | $/KWH | Unit 17-Gas Turbine (21.9 MW) | 19377.42 | 19550.39 | 17.61%
Power Fuel Cost (to bus) | 0.16575 | 0.16297 |  | $/KWH | Unit 19-Gas Turbine (24.5 MW) | 25705.17 | 28434.32 | 13.27%
Water Fuel Cost (Internal) | 1.8579 | 1.8466 |  | $/KGAL | Unit 20_Gas Turbine (24.5 MW) | 0 | 0 | 0%
Water Fuel Cost (to Distribution) | 1.8973 | 1.8847 |  | $/KGAL | Aggreko (20.0 MW) | 10962.74 | 10925.01 | 31.12%
Total Power Fuel Cost | 3815559.4954 | 3764437 | 7528873.9999 | $ | Total Electric Generation Only | 15206.09 | 15153.17 | 22.44%
Total Water Cost | 165576.8536 | 166287.26 | 332574.5201 | $ | *Note:Total Electric Generation includes values of steam provided to STG #10 and #11 by HRSGs
Propane consumed | 85397.8095 | 87722.5119 | 175445.0238 | BBLS
No. 2 Fuel Consumed | 9234.3241 | 7377.2245 | 14754.449 | BBLS
[5 empty] | Power Units Availability |  | FYTD
No. 2 Fuel Received | 32182.12 | 32182.12 | 32182.12 | BBLS |  | This Month | AVG.
[5 empty] | Unit | Percent (%) | Percent (%)
EOM No. 2 Fuel On Hand* | 28.5841 | 22.8472 |  | DAYS
Plant Water Use ( Internal | 1941.8664 | 8680.5887 | 17361.1773 | $ | Unit 10 | 0% | 0%
Plant Power Use (Internal) | 281664.3417 | 279028.9535 | 558057.907 | $ | Unit 11 | 0% | 0%
7SEAS RO 1 Electricity Cost | 75610.3018 |  |  | $ | Unit 16 | 0% | 0%
7SEAS UPW Electricity Cost | 2720.5084 |  |  | $ | Unit 17 | 100% | 100%
7SEAS RO 2 Electricity Cost | 89966.5518 |  |  | $ | Unit 19 | 100% | 100%
**Note: Includes power generated by solar |  |  |  |  | Unit 20 | 0% | 0%
*Note: Based on 2000Bbl/day consumption |  |  |  |  | Aggreko | 100% | 100%
[5 empty] | HRSG 21 | 0% | 0%
[5 empty] | HRSG 24 | 100% | 100%

## PR-Pag2
August - 2020
Power Generation - Station Power |  | FYTD | TOTAL | Generating Units Average Loading |  |  | FYTD | Utilization
Item | This Month | Monthly | FYTD |  |  | This Month | AVG. | Factor
| KWH | AVG. | KWH | (KWH / Operating Hours) |  | KW | KW | Percent
Steam Turbine Generation | 0 | 0 | 0 | Unit 10 |  | 0 | 0 | 0%
Gas Turbine Generation | 25132080 | 25104015 | 50208030 | Unit 11 |  | 0 | 0 | 0%
Diesel Generation | 0 | 0 | 0 | Unit 16 |  | 0 | 0 | 0%
Total Generation | 25132080 | 25104015 | 50208030 | Unit 17 |  | 13655.7831 | 13639.4669 | 62.36%
Steam Station Power | 0 | 0 | 0 | Unit 19 |  | 6600.6601 | 5576.8431 | 26.94%
Gas Turbine Station Power | 45350 | 45370 | 90740 | Unit 20 |  | 0 | 0 | 0%
Aggreko Station Service | 200 | 230 | 460 | Aggreko |  | 19600 | 19745 | 98%
Total Gen. Plant Station Power | 45350 | 45370 | 90740 | Diesel |  | 0 | 0 | 0%
Total Service / Gross Output | 0.1804% | 0.1807%
IPP1 | 664983.5 | 654511.5 | 1309023
Total System Generation | 25797063.5 | 25104015 | 50208030
Generating Units Station Power
Generating Units Operating Hours |  | FYTD | TOTAL |  |  | FYTD | TOTAL | This Month | FYTD | FYTD
| This Month | Monthly | FYTD |  | This Month | AVG. | FYTD | SS Power | AVG. | SS Power
Unit | HRS | AVG. | HRS | Unit | KWH | KWH | KWH | KWH | KWH | KWH
Unit 10 | 0 | 0 | 0 | Unit 10 | 0 | 0 | 0 | 0 | 0 | 0
Unit 11 | 0 | 0 | 0 | Unit 11 | 0 | 0 | 0 | 0 | 0 | 0
Unit 16 | 0 | 0 | 0 | Unit 16 | 0 | 0 | 0 | 0 | 0 | 0
Unit 17 | 722.8 | 731.15 | 1462.3 | Unit 17 | 9870400 | 9972360 | 19944720 | 3560 | 2965 | 5930
Unit 19 | 242.4 | 211.25 | 422.5 | Unit 19 | 1600000 | 1210000 | 2420000 | 34800 | 35160 | 70320
Unit 20 | 0 | 0 | 0 | Unit 20 | 0 | 0 | 0 | 6990 | 7245 | 14490
Aggreko | 697.0245 | 705.0138 | 1410.0275 | Aggreko | 13661680 | 13921655 | 27843310 | 200 | 230 | 460
Diesel Generation(Emergency) | 3 | 2 | 4 | Diesel | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | TOTAL | 25132080 | 25104015 | 50208030 | 45350 | 45370 | 90740

## PR-Pag3
August - 2020
BOILERS/STM. TURBINES | SS | GAS TURBINE | SS | STX. EMERGENCY DIESEL | SS | OTHERS | SS
| Kwh |  | Kwh |  | Kwh |  | Kwh
SS10 Plant Aux. Trans 480V | 0 | Plant SS |  | Diesel | 0 | Station Service Shops | 31680
SS10 Unit Aux.. Trans 480V | 0 | Unit 16 | 0 |  |  | Station Service Office | 0
|  | Unit 17 | 980 |  |  | Fuel Tanks SS | 0
Unit 10 Total Station Power | 0 | Unit 19 | 34800 | TOTAL DIESEL | 0 | Switch Yard SS | 161120
|  | Unit 20 | 5490 |  |  | Richmond Sub SS
|  | Aggreko | 200 |  |  | Midland Sub SS
SS11 Plant Aux. Trans 480V | 0 |  |  |  |  | TOTAL OTHERS | 192800
SS11 Unit Aux.. Trans 480V | 0 | Unit SS |  | WATER PLANTS | SS
|  | Unit 16 | 0 |  | Kwh | SwitchGear Bkr1 SS | 1097708.5
Unit 11 Net Total Station Power | 0 | Unit 17 | 2580 | Plant ABC Pump usage | 0 | SwitchGear Bkr3 SS | 306636
|  | Unit 19 | 0 |  |  | SS10 Unit Aux Trans. | 0
|  | Unit 20 | 1500 | Intake Pump A&B+Chloropac | 0 | SS11 Unit Aux Trans. | 0
HRSG 21 Station Power | 0 | TOTAL GAS TURBINES | 45550 |  |  | Total GT Unit SS | 4080
HRSG 24 Station Power** | 0 | Plant Pumps |  | RO Plant Electrical Usage | 477312
|  | Intake Pump A | 0 | UPW Electrical Usage | 17174 |  | 1408424.5
|  | Intake Pump B | 0 | RO ANNEX Electrical Usage | 567940
WHB Net Station Power | 0 | Intake Pump C | 0
TOTAL BOILERS / STM TURBINES | 0 |  |  | TOTAL WATER PLANTS | 1062426 | Total Station Service* | 1300776
*Total SS switched to a summaton of individual meters from general 'main' distribution meters summation
** No power to meter

## PR-Pag4
August - 2020
Desalination Plants Summary
|  | FYTD | TOTAL | Units Water Output
| Service | AVG. | FYTD | This Month | FYTD
Unit | HRS | HRS | HRS | GALS | GALS
RO 1 |  |  |  | 39612500 | 77065500
RO 2 |  |  |  | 49509333.3333 | 103043666.6667
STX TOTALS |  |  |  | 89121833.3333 | 180109166.6667
Boilers Summary
|  | Boilers Service Hours |  |  | Make Up Feed Water |  | Low Pressure Steam |  | High Pressure Steam
| Service | AVG. | FYTD | This Month | AVG. | FYTD | This Month | FYTD | This Month | FYTD
Unit | HRS | HRS | HRS | GALS | GALS | GALS | LBS | AVG. | LBS | AVG.
HRSG 21/IPOS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HRSG 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Boiler 11 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
TOTALS |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Distribution |  | This Month | FYTD-AVG. | FYTD |  | Steam Summary |  | LP Steam | HP Steam
|  | GALS | GALS | GALS |  | ITEM |  | LBS | LBS
Total Plant Water Produced |  | 89121833.3333 | 90054583.3333 | 180109166.6667 |  | Total Steam Produced |  | 0 | 0
Total Reverse Osmosis Produced |  | 89121833.3333 | 38532750 | 77065500 |  | To Steam Turbine 10 |  |  | 0
Total to Distribution Tank |  | 87271346.6667 | 88238876.6667 | 176477753.3333 |  | To Steam Turbine 11 |  |  | 0
Apparent Station Use |  | 1850486.6667 | 1815706.6667 | 3631413.3333 |  | From Steam Turbine 10 |  | 0 | 0
Water to day Tank |  | 1244333.3333 | 1197833.3333 | 2395666.6667 |  | From Steam Turbine 11 |  | 0
UPW Feed |  | 1833186.6667 | 1793606.6667 | 3587213.3333
UPW Product |  | 1244333.3333 | 1197833.3333 | 2395666.6667 |  | Used Steam for Production |  | 0 | 0
Water to the Demineralizer (Regen) |  | 0 | 0 | 0 |  | Others uses & Deareator |  |  | 0
Boilers Make Up |  | 0 | 0 | 0
Unit 16 Noxwater |  | 0 | 0 | 0
Unit 17 Noxwater |  | 813283.4473 | 4525597.3511 | 9051194.7021
Unit 19 Noxwater |  | 214627.1973 | 175451.6602 | 350903.3203
Unit 20 Noxwater |  | 0 | 0 | 0
Metered Total Wtr to NOX |  | 1094100 | 1050800 | 2101600
Station Wtr Warehouse & Eng. |  | 0 | 0 | 0
Plant Service Water |  | 17300 | 22100 | 44200
Admin. Off. Water |  | 0 | 0 | 0
WTR to Fire Hydrants |  | 0 | 0 | 0 |  | * Unaccountable value has been zeroed due to non-functional distribution
Total Water used |  | 1850486.6667 | 1815706.6667 | 3631413.3333 |  |  | meter giving rise to high unaccountable value
Unaccountable Water |  | 0 | 0 | 0

## PR-Pag5
August - 2020
| Feeders Power Distribution |  | This Month Total Plant Outages |  |  | Month | FYTD | FYTD | Feeders Outages Summary
| Output | FYTD | Planned | Forced | Time Hrs | Lost Sales | Total | Total | Feeder | Time | Date | Reason
Feeder | KWH | AVG KWH | Outages | Outages | Duration | Kwh | Outages | Time Hrs |  | min.
[9 empty] | Feeder #1A | 131 | 2020-08-08 | After a switching order,splicing sleeve on "A" phase on feeder 2A came loose and blew
Feeder #1A (13Kv) | 1358974.88 | 1359734.75 | 0 | 2 | 2.25 | 4122.2696 | 2 | 2.6667 | Feeder #2A | 943 | 2020-08-08 | After a switching order,splicing sleeve on "A" phase on feeder 2A came loose and blew
Feeder #2A (13 Kv) | 3157129.75 | 3199480.655 | 0 | 2 | 15.9167 | 69018.1735 | 11 | 17.6667 | Feeder #3A | 138 | 2020-08-08 | After a switching order,splicing sleeve on "A" phase on feeder 2A came loose and blew
Feeder #3A (13(Kv) | 1126770 | 1119222 | 0 | 3 | 4.35 | 6626.7147 | 3 | 4.7833 | Feeder #4A | 146 | 2020-08-08 | After a switching order,splicing sleeve on "A" phase on feeder 2A came loose and blew
Feeder #4A (13 Kv) | 1558387 | 1550351.875 | 0 | 3 | 3.0167 | 6344.4532 | 3 | 3.8333 | Feeder #5A | 130 | 2020-08-08 | After a switching order,splicing sleeve on "A" phase on feeder 2A came loose and blew
Feeder #5A (13 Kv) | 3720000 | 3805000 | 0 | 2 | 2.2333 | 11200.2876 | 2 | 2.65 | Feeder #6A | 169 | 2020-08-08 | After a switching order,splicing sleeve on "A" phase on feeder 2A came loose and blew
Feeder #6A (13 Kv) | 2244390 | 2258583.5 | 0 | 1 | 2.8167 | 8529.1968 | 0 | 3.65 | Feeder #8B | 137 | 2020-08-08 | After a switching order,splicing sleeve on "A" phase on feeder 2A came loose and blew
Feeder #9A (13 Kv) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Feeder #9B | 170 | 2020-08-08 | After a switching order,splicing sleeve on "A" phase on feeder 2A came loose and blew
Feeder #6B (24 Kv) | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 3.6667 | Feeder #10A | 173 | 2020-08-08 | After a switching order,splicing sleeve on "A" phase on feeder 2A came loose and blew
Feeder #8B (24 Kv) | 5863816.5 | 5431478 | 0 | 1 | 2.2833 | 18051.4316 | 4 | 3.6667 | Feeder #10B | 173 | 2020-08-08 | After a switching order,splicing sleeve on "A" phase on feeder 2A came loose and blew
Feeder #9B(24Kv) | 2607787.671 | 3441006.4605 | 0 | 1 | 2.8333 | 9969.0556 | 2 | 4.9333 | Feeder #1A | 4 | 2020-08-08 | Unit 17 tripped off line
Feeder #10A(24Kv) | 832165 | 832165 | 0 | 0 | 0 | 0 | 0 | 0 | Feeder #5A | 4 | 2020-08-08 | Unit 17 tripped off line
Feeder #10B(24Kv) | 1548799.5 | 1540490.25 | 0 | 4 | 6.5667 | 13791.6875 | 4 | 6.5667 | Feeder #2A | 12 | 2020-08-08 | Feeders tripped due to insufficient generation
TOTALS | 24018220.301 | 24537512.4905 | 0 | 19 | 42.2667 | 147653.2701 | 35 | 54.0833 | Feeder #3A | 3 | 2020-08-08 | Feeders tripped due to insufficient generation
[9 empty] | Feeder #4A | 12 | 2020-08-08 | Feeders tripped due to insufficient generation
[9 empty] | Feeder #10A | 119 | 2020-08-13 | Feeders tripped due to insufficient generation
[9 empty] | Feeder #10B | 4 | 2020-08-13 | Feeders tripped due to insufficient generation
[9 empty] | Feeder #4A | 23 | 2020-08-13 | Feeder opened to maintain frequency and scheduled power rotation
[9 empty] | Feeder #10A | 94 | 2020-08-13 | Feeder opened to maintain frequency and scheduled power rotation
[9 empty] | Feeder #10B | 31 | 2020-08-13 | Feeder opened to maintain frequency and scheduled power rotation
[9 empty] | Feeder #3A | 120 | 2020-08-13 | Feeder opened to maintain frequency and scheduled power rotation
[9 empty] | Feeder #10B | 5 | 2020-08-14 | Feeder opened to maintain frequency and scheduled power rotation
[9 empty] | Feeder #10A | 8 | 2020-08-23 | Feeders tripped while conducting load test on Unit 17
[9 empty] | Feeder #10B | 5 | 2020-08-23 | Feeders tripped while conducting load test on Unit 17
0
0
0
0
0

## PR-Pag6
August - 2020
Power - Water Units Outages
|  | TOTAL NUMBER OF OUTAGES |  |  |  | PLANNED OUTAGES |  |  |  | FORCED OUTAGES
| This Month | FYTD | This Month | FYTD | This Month | FYTD | Duration | FYTD | This Month | FYTD | Duration | FYTD
Unit | Outages | Outages | Hours | Hours | Outages | Outages | Hours | Hours | Outages | Outages | Hours | Hours
Unit 10ST | 1 | 2 | 744 | 1488 | 1 | 2 | 744 | 1488 | 0 | 0 | 0 | 0
Unit 11ST | 1 | 2 | 744 | 1488 | 1 | 2 | 744 | 1488 | 0 | 0 | 0 | 0
Unit11BLR | 1 | 2 | 744 | 1488 | 1 | 2 | 744 | 1488 | 0 | 0 | 0 | 0
Unit 16 | 0 | 0 | 744 | 1488 | 0 | 0 | 744 | 1488 | 0 | 0 | 0 | 0
Unit 17 | 1 | 2 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0
Unit 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Unit 20 | 1 | 2 | 744 | 1488 | 1 | 2 | 744 | 1488 | 0 | 0 | 0 | 0
Aggreko | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HRSG 21 | 1 | 2 | 744 | 1488 | 1 | 2 | 744 | 1488 | 0 | 0 | 0 | 0
HRSG 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTALS | 6 | 12 |  |  | 6 |  |  |  | 0 | 0
Plant Power Distribution
|  |  | This Month | FYTD | FYTD |  |  |  | Peak and Min. Load Data
|  |  | KWH | KWH | AVG. | [5 empty] | FYTD
Total 13KV Feeders |  |  | 13165651.63 | 26584745.56 | 13292372.78 |  |  |  |  | This Month | AVG.
Total 24KV Feeders |  |  | 10852568.671 | 21658114.421 | 10829057.2105 |  |  | Peak Load (KW) |  | 41790 | 41435
Feeder Totals |  |  | 24018220.301 | 48242859.981 | 24121429.9905 |  |  | Day |  | Sunday
Total Generation |  |  | 25797063.5 | 51517053 | 25758526.5 |  |  | Date |  | 2020-08-16
T1,T3,T4, T5, T6, T7 Available |  |  | 109683814 | 119659822 | 59829911 |  |  | Hour |  | 19:21
T1&T3&T4&T5&T6&T7 Losses* |  |  | 366338.699 | 414007.769 | 207003.8845
Net Distributed |  |  | 25430724.801 | 51103045.231 | 25551522.6155 |  |  | Min. Load (KW) |  | 26320 | 26985
Line Department |  |  |  | 0 | 0 |  |  | Day |  | Wednesday
Water Department |  |  |  | 0 | 0 |  |  | Date |  | 2020-08-05
Power Plant Services |  |  |  | 0 | 0 |  |  | Hour |  | 6:00
Administration & General |  |  |  | 0 | 0
Plant Station Service |  |  |  | 0 | 0
Net Available from Bus |  |  |  | 0 | 0
Wapa KWH From Dist |  |  |  | 0 | 0 |  | * meters under review
SwitchGear Bkr1 SS |  |  | 1097708.5 | 2224421 | 1112210.5
SwitchGear Bkr3 SS |  |  | 306636 | 607924.25 | 303962.125
Total Station Service Power |  |  | 1300776 | 2846265.25 | 1423132.625
Net KWH Available for Sale |  |  | 24022300.301 | 48256779.981 | 24128389.9905
Plant Unaccountable |  |  | 0 | 0 | 0
0
0
0
0
0

## PR-Pag7
August - 2020
|  |  | Fuel Allocation | BBLS
|  |  | Propane Fuel For Power | 85397.8095
|  |  | Propane Fuel For Water | 0
|  |  | No 2 Fuel For Power | 9234.3241
|  |  | No 2 Fuel For Water | 0
|  |  | O&M Factor for Water | 0
Power Boilers
11
TPBSFC
BLR11FUELCOST
0 |  | GT Fuel Allocation
HP Stm from WHB
GTFCAE
WHBHPSTMCOST
Combined Cycle |  | 0
WHB, 16. 17. 20
TGTFC |  |  |  |  | Electrc Power
GEN1617FUELCOST |  |  |  |  | Generation
1941412.8559 |  |  |  |  | TOTFUELCOSTPWR
|  |  | Gas Turbine |  | 3815559.4954
Power Allocation
Simple Cycle |  |  | GTFCA
GEN161720ADJFCOST
GEN 19 FUELCOST |  |  | 1941412.8559
552396.4641
RO Water
DIESEL |  |  |  |  | Production Cost
Emergency Gen.
DIESEL_EMER. |  |  |  |  | 165576.8536
0
*Note: The fuel prices in this report are an estimation
Cost Calculated at:
| 77.2818 | per BBL for No. 2
| 38.262 | per BBL for Propane

## PR-Pag8
August - 2020
Fuel Allocations
Fuel Summary |  |  |  | ITEM | Amount | FYTD
ITEM | Propane | No2 BBLS
|  |  |  | Electric Power Generation | 3815559.4954 | 7528873.9999
Inventory-Beginning of Month |  | 34220.4379 |  | Water Production* | 165576.8536 | 332574.5201
Received During Month |  | 32182.12 |  | Total #2 Fuel Cost | 713645.361 | 1140250.6564
Consumed During Month |  | 9234.3241 |  | BBLS Propane for Power | 85397.8095 | 175445.0238
Inventory-End of Month |  | 57168.2338 |  | BBLS Propane for Water | 0 | 0
Calorific Value (BTU/GAL) | 91735 | 136999.0879 |  | BBLS No. 2 for Power | 9234.3241 | 14754.449
|  |  |  | BBLS No.2 for Water | 0 | 0
|  |  |  | Propane BBL Cost | 38.262
End of Month- Fuel in Tanks |  |  |  | No. 2 BBL Cost | 77.2818
|  | No 2 BBLS |  | * Note: Includes RO Electric Usage
|  |  |  | No. 2 Oil Used | This Month | FYTD
Tank 1 |  | 0 |  | No. 2 Units | BBLS No. 2 | BBLS No. 2
Tank 2 |  | 0
Tank 3 |  | 4450.29 |  | Unit 11 | 0 | 0
Tank 4 |  | 3936.1 |  | Unit 16 | 0 | 0
Tank 5 |  | 37021.4 |  | Unit 17 | 2086.5049 | 3158.5338
Tank 6 |  | 11760.45 |  | Unit 19 | 7147.8192 | 11595.9153
Tank 7 |  |  |  | Unit 20 | 0 | 0
TOTALS | 0 | 57168.2338 |  | Diesel Emergency | 0 | 0
|  |  |  | Total No. 2 Consumed | 9234.3241 | 14754.449
Fuel Shipments |  |  |  | Propane Used | This Month | FYTD
|  | No2 | No2 | Propane Units | Gals | Gals
|  | Date | BBLS | Unit 16 | 0 | 0
|  | 44062 | 32182.12 | Unit 17 | 1954076.7936 | 4052956.7682
|  |  |  | Unit 20 | 0 | 0
|  |  |  | Aggreko | 1632631.2064 | 3315734.2318
|  |  |  | Total Propane Consumed | 3586708 | 7368691
TOTAL SHIPMENTS |  |  | 32182.12
|  |  |  | Tank Fuel / Metered Fuel | Ratio
Used Oil recovered | 0 | Bbls
|  |  |  | No. 2 | 1.0382
|  |  |  | Propane | 0.97193
Ratio 0.95 to 1.05 acceptable
0
0
0
0
0

## PR-Pag9
August - 2020

## PR-Pag10
August - 2020

## PR-Pag11
August - 2020