## DataBase
FISCAL YEAR 2020-2021
|  | 31 | 31 | 30 | 31 | 30 | 31 | 31 | 28 | 31 | 30 | 31 | 0
|  | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY | JUN | FYTD | FYTD-AVG
Item | Index | 7 | 8 | 9 | 10 | 12 | 12 | 13 | 14 | 15 | 16 | 17 | 18
Total System Generation |  | 7: 25719.9895; 8: 25797.0635; 9: 24243.5125; 10: 24404.586; 12: 22938.64; 12: 22207.3064 | 145311.0979 | 24218.5163
Gross Power Generation |  | 7: 25075.95; 8: 25132.08; 9: 23591.11; 10: 23735.79; 12: 22338.04; 12: 21615.68 | 141488.65 | 23581.4417
Gross Water Production |  | 7: 90987.3333; 8: 89121.8333; 9: 82706.1667; 10: 88049.8333; 12: 87245.3333; 12: 88737.3333 | 526847.8333 | 87807.9722
System Load Factor |  | 7: 82.05%; 8: 80.83%; 9: 81.77%; 10: 81.1%; 12: 78.74%; 12: 77.83% | 482.3% | 80.39%
Total No. 6 Fuel Cost |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Total No. 2 Fuel Cost |  | 7: 426605.2954; 8: 639765.748; 9: 1161061.1421; 10: 134059.983; 12: 151618.4179; 12: 142478.9617 | 2655589.548 | 442598.258
Total Propane Cost |  | 7: 3453706.8756; 8: 3267490.988; 9: 2553332.1795; 10: 3331088.4222; 12: 3278983.919; 12: 3545434.9632 | 19430037.3475 | 3238339.5579
Power Fuel Cost (Internal) |  | 7: 0.15474; 8: 0.15547; 9: 0.15745; 10: 0.14599; 12: 0.15358; 12: 0.17061 | 0.93784 | 0.15631
Power Fuel Cost (to bus) |  | 7: 0.16018; 8: 0.16268; 9: 0.16406; 10: 0.15209; 12: 0.16122; 12: 0.17696 | 0.97719 | 0.16287
Water Fuel Cost (Internal) |  | 7: 1.8354; 8: 1.8234; 9: 1.8371; 10: 1.6996; 12: 1.7806; 12: 1.9944 | 10.9705 | 1.8284
Water Fuel Cost (to Distribution |  | 7: 1.872; 8: 1.8621; 9: 1.8651; 10: 1.7235; 12: 1.812; 12: 2.0305 | 11.1652 | 1.8609
Total Power Fuel Cost |  | 7: 3713314.5045; 8: 3744752.5614; 9: 3562453.9143; 10: 3315497.8093; 12: 3275251.6783; 12: 3510940.5724 | 21122211.0402 | 3520368.5067
Total Water Fuel Cost |  | 7: 166997.6665; 8: 162504.1747; 9: 151939.4073; 10: 149650.5959; 12: 155350.6585; 12: 176973.3525 | 963415.8553 | 160569.3092
No. 6 Fuel Consumed |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
No. 2 Fuel Consumed |  | 7: 5520.1249; 8: 9234.3241; 9: 16758.6572; 10: 1935.0103; 12: 2188.4473; 12: 2056.614 | 37693.1779 | 6282.1963
No. 6 Fuel Received |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
No. 2 Fuel Received |  | 7: 0; 8: 32182.12; 9: 0; 10: 0; 12: 0; 12: 0 | 32182.12 | 32182.12
EOM No. 6 Fuel On Hand |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
EOM No. 2 Fuel On Hand(based on 2000Bbl/day Consumption) |  | 7: 17.1102; 8: 28.5841; 9: 20.2048; 10: 19.2373; 12: 18.1431; 12: 17.1148 | 120.3942 | 20.0657
Plant Water Use ( Internal) |  | 7: 15419.311; 8: 1905.8303; 9: 2090.0527; 10: 1555.6764; 12: 1504.9232; 12: 8461.1204 | 30936.9139 | 5156.1523
Plant Power Use (Internal) |  | 7: 276393.5654; 8: 276437.3787; 9: 254105.137; 10: 251337.0171; 12: 256049.3028; 12: 300074.1452 | 1614396.5461 | 269066.091
Heat Rates BTU/KWH | [13 empty] | 0 | 0
(Net Energy in KWH Produced) | [13 empty] | 0 | 0
Units | [13 empty] | 0 | 0
Combined Cycle-Units 10,16 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Combined Cycle-Units 11,16 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 10-Steam (10 MW) |  | 7: N/A; 8: N/A; 9: N/A; 10: N/A; 12: N/A; 12: N/A | 0 | 0
Unit 11-Steam (21 MW) |  | 7: N/A; 8: N/A; 9: N/A; 10: N/A; 12: N/A; 12: N/A | 0 | 0
Unit 16-Gas Turbine (23 MW) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 17-Gas Turbine (20.3 MW) |  | 7: 19723.3655; 8: 19377.4218; 9: 19918.1643; 10: 20433.9315; 12: 20902.8681; 12: 21861.1136 | 122216.8648 | 20369.4775
Unit 19-Gas Turbine (24 MW) |  | 7: 31163.4711; 8: 25705.1735; 9: 19292.4251; 10: 22369.8317; 12: 21548.3601; 12: 24977.4508 | 145056.7123 | 24176.1187
Unit 20_Gas Turbine (24 MW) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 41467.1816 | 41467.1816 | 41467.1816
Aggreko |  | 7: 10887.2856; 8: 10962.7384; 9: 10998.875; 10: 10904.2078; 12: 10898.0236; 12: 10911.9193 | 65563.0498 | 10927.175
Total Plant . |  | 7: 15100.2454; 8: 15206.0874; 9: 15197.1983; 10: 14624.6701; 12: 14782.9218; 12: 15044.4226 | 89955.5457 | 14992.5909
Desal Performance Ratios | [13 empty] | 0 | 0
IDE3 (1.25MGD) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE4 (.55MGD) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE5 (0.55MGD) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE9 (1.3MGD) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit Availability Percent | [13 empty] | 0 | 0
Unit 10 | [13 empty] | 0% | 0% | bar: 7 to 12
Unit 11 | [13 empty] | 0% | 0% | bar: 7 to 12
Unit 16 | [13 empty] | 0% | 0% | bar: 7 to 12
Unit 17 |  | 7: 100%; 8: 100%; 9: 96.3%; 10: 100%; 12: 100%; 12: 100% | 596.3% | 99.38%
Unit 19 |  | 7: 100%; 8: 100%; 9: 100%; 10: 100%; 12: 100%; 12: 100% | 600% | 100%
Unit 20 |  | 7: 0%; 8: 0%; 9: 0%; 10: 0%; 12: 0%; 12: 2.78% | 2.78% | 0.4633%
Aggreko |  | 7: 100%; 8: 100%; 9: 100%; 10: 100%; 12: 100%; 12: 100% | 600% | 100%
IDE 3 |  | 7: 100%; 8: 100%; 9: 100%; 10: 100%; 12: 100%; 12: 100% | 600% | 100%
IDE 4 | [13 empty] | 0% | 0% | bar: 7 to 12
IDE 5 | [13 empty] | 0% | 0% | bar: 7 to 12
IDE 9 |  | 7: 100%; 8: 100%; 9: 100%; 10: 100%; 12: 100%; 12: 100% | 600% | 100%
HRSG 21 | [13 empty] | 0% | 0% | bar: 7 to 12
HRSG 24 |  | 7: 100%; 8: 100%; 9: 100%; 10: 100%; 12: 100%; 12: 100% | 600% | 100%
Pag2 | [13 empty] | 0 | 0
Item | [13 empty] | 0 | 0
Steam Turbine Generation |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Gas Turbine Generation |  | 7: 25075950; 8: 25132080; 9: 23591110; 10: 23735790; 12: 22338040; 12: 21615680 | 141488650 | 23581441.6667
Diesel Generation |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Total Generation |  | 7: 25075950; 8: 25132080; 9: 23591110; 10: 23735790; 12: 22338040; 12: 21615680 | 141488650 | 23581441.6667
IPP1 |  | 7: 644039.5; 8: 664983.5; 9: 652402.5; 10: 668796; 12: 600600; 12: 591626.406 | 3822447.906 | 637074.651
Total System Generation |  | 7: 25719989.5; 8: 25797063.5; 9: 24243512.5; 10: 24404586; 12: 22938640; 12: 22207306.406
Steam Station Power |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Gas Turbine Station Power |  | 7: 45390; 8: 45350; 9: 49610; 10: 36910; 12: 35210; 12: 62750 | 275220 | 45870
Total Gen. Plant Station Power |  | 7: 45390; 8: 45350; 9: 49610; 10: 36910; 12: 35210; 12: 62750 | 275220 | 45870
Total Service / Gross Output |  | 7: 0.181%; 8: 0.1804%; 9: 0.2103%; 10: 0.1555%; 12: 0.1576%; 12: 0.2903% | 1.175% | 0.1959%
Operating Hours | [13 empty] | 0 | 0
Unit 10 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 11 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 16 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 17 |  | 7: 739.5; 8: 722.8; 9: 610.5; 10: 728.2; 12: 704.3; 12: 727.4 | 4232.7 | 705.45
Unit 19 |  | 7: 180.1; 8: 242.4; 9: 287.9; 10: 41.9; 12: 58.7; 12: 29.4 | 840.4 | 140.0667
Unit 20 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 19.6 | 19.6 | 19.6
Aggreko |  | 7: 713.003; 8: 697.0245; 9: 639.6298; 10: 741.0772; 12: 691.7374; 12: 728.6257 | 4211.0976 | 701.8496
Diesel Generation(Emergency) |  | 7: 1; 8: 3; 9: 0; 10: 3; 12: 1; 12: 1 | 9 | 1.8
Unit Average Loading | [13 empty] | 0 | 0
(KWH / Operating Hours) | [13 empty] | 0 | 0
Unit 10 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 11 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 16 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 17 |  | 7: 13623.1508; 8: 13655.7831; 9: 13025.7166; 10: 12180.1154; 12: 11559.9035; 12: 10267.5282 | 74312.1975 | 12385.3662
Unit 19 |  | 7: 4553.0261; 8: 6600.6601; 9: 11774.9218; 10: 7875.895; 12: 8517.8876; 12: 7142.8571 | 46465.2477 | 7744.208
Unit 20 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 7677.551 | 7677.551 | 7677.551
Aggreko |  | 7: 19890; 8: 19600; 9: 19150; 10: 19615; 12: 19800; 12: 18921.375 | 116976.375 | 19496.0625
Diesel |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Utilization Factor | [13 empty] | 0 | 0
Unit 10 | [13 empty] | 0% | 0% | bar: 7 to 12
Unit 11 | [13 empty] | 0% | 0% | bar: 7 to 12
Unit 16 | [13 empty] | 0% | 0% | bar: 7 to 12
Unit 17 |  | 7: 62.21%; 8: 62.36%; 9: 59.48%; 10: 55.62%; 12: 52.78%; 12: 46.88% | 339.3% | 56.55%
Unit 19 |  | 7: 18.58%; 8: 26.94%; 9: 48.06%; 10: 32.15%; 12: 34.77%; 12: 29.15% | 189.7% | 31.61%
Unit 20 |  | 7: 0%; 8: 0%; 9: 0%; 10: 0%; 12: 0%; 12: 31.34% | 31.34% | 31.34%
Aggreko |  | 7: 99.45%; 8: 98%; 9: 95.75%; 10: 98.08%; 12: 99%; 12: 94.61%
Diesel | 1 | [12 empty] | 0% | 0% | bar: 7 to 12
Unit Output KW | 2 | [12 empty] | 0 | 0
Unit 10 | 3 | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 11 | 4 | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 16 | 5 | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 17 | 6 | 7: 10074320; 8: 9870400; 9: 7952200; 10: 8869560; 12: 8141640; 12: 7468600 | 52376720 | 8729453.3333
Unit 19 | 7 | 7: 820000; 8: 1600000; 9: 3390000; 10: 330000; 12: 500000; 12: 210000 | 6850000 | 1141666.6667
Unit 20 | 8 | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 150480 | 150480 | 150480
Aggreko |  | 7: 14181630; 8: 13661680; 9: 12248910; 10: 14536230; 12: 13696400; 12: 13786600 | 82111450 | 13685241.6667
Diesel |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
TOTAL | 9 | 7: 25075950; 8: 25132080; 9: 23591110; 10: 23735790; 12: 22338040; 12: 21615680 | 141488650 | 23581441.6667
Unit Station Service Power | [13 empty] | 0 | 0
Unit 10 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 11 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 16 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 17 |  | 7: 2370; 8: 3560; 9: 6150; 10: 2820; 12: 2490; 12: 2640 | 20030 | 3338.3333
Unit 19 |  | 7: 35520; 8: 34800; 9: 36960; 10: 27680; 12: 27120; 12: 27440 | 189520 | 31586.6667
Unit 20 |  | 7: 7500; 8: 6990; 9: 6500; 10: 6410; 12: 5600; 12: 32670 | 65670 | 10945
Aggreko |  | 7: 260; 8: 200; 9: 2350; 10: 670; 12: 230; 12: 400 | 4110 | 685
Diesel |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
TOTAL |  | 7: 45390; 8: 45350; 9: 49610; 10: 36910; 12: 35210; 12: 62750 | 275220 | 45870
pag3 | [13 empty] | 0 | 0
BOILERS/STM. TURBINES | [13 empty] | 0 | 0
[14 empty] | 0 | 0
SS10 Plant Aux. Trans 480V |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
SS10 Unit Aux.. Trans 480V |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
[14 empty] | 0 | 0
Unit 10 Total Station Power |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
SS11 Plant Aux. Trans 480V |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
SS11 Unit Aux.. Trans 480V |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
[14 empty] | 0 | 0
Unit 11 Net Total Station Power |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
HRSG 21 Station Power |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
HRSG 24 Station Power |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
WHB Net Station Power |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
TOTAL BOILERS / STM TURBINES |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
GAS TURBINE | [13 empty] | 0 | 0
[14 empty] | 0 | 0
Plant SS | [13 empty] | 0 | 0
Unit 16 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 17 |  | 7: 30; 8: 980; 9: 4410; 10: 780; 12: 690; 12: 600 | 7490 | 1248.3333
Unit 19 |  | 7: 35520; 8: 34800; 9: 36960; 10: 27680; 12: 27120; 12: 27440 | 189520 | 31586.6667
Unit 20 |  | 7: 0; 8: 5490; 9: 6500; 10: 6410; 12: 5600; 12: 32670 | 56670 | 11334
|  | 7: 260; 8: 200; 9: 2350; 10: 670; 12: 230; 12: 400 | 4110 | 685
Unit SS | [13 empty] | 0 | 0
Unit 16 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 17 |  | 7: 2340; 8: 2580; 9: 1740; 10: 2040; 12: 1800; 12: 2040 | 12540 | 2090
Unit 19 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 20 |  | 7: 7500; 8: 1500; 9: 0; 10: 0; 12: 0; 12: 0 | 9000 | 4500
|  | 7: 9840; 8: 4080; 9: 1740; 10: 2040; 12: 1800; 12: 2040 | 21540 | 3590
Plant IDE pumpage | [13 empty] | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
[14 empty] | 0 | 0
Total |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
TOTAL GAS TURBINES |  | 7: 45650; 8: 45550; 9: 51960; 10: 37580; 12: 35440; 12: 63150 | 279330 | 46555
STX. EMERGENCY DIESEL | [13 empty] | 0 | 0
[14 empty] | 0 | 0
Diesel |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
TOTAL DIESEL |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
WATER PLANTS | [13 empty] | 0 | 0
[14 empty] | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Intake Pump A |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Intake Pump B |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Intake Pump C |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE Intake Pumps A&B+Chloropac |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
RO Plant |  | 7: 458594; 8: 477312; 9: 395292; 10: 448162; 12: 427195; 12: 459956 | 2666511 | 444418.5
UPW Electricity |  | 7: 17911; 8: 17174; 9: 15510; 10: 15316; 12: 14254.62; 12: 14855 | 95020.62 | 15836.77
RO ANNEX Electricity |  | 7: 620604; 8: 567940; 9: 569716; 10: 576924; 12: 584356; 12: 577324 | 3496864 | 582810.6667
TOTAL WATER PLANTS |  | 7: 1097109; 8: 1062426; 9: 980518; 10: 1040402; 12: 1025805.62; 12: 1052135 | 6258395.62 | 1043065.9367
OTHERS | [13 empty] | 0 | 0
[14 empty] | 0 | 0
Station Service Shops |  | 7: 25440; 8: 31680; 9: 29640; 10: 27480; 12: 26160; 12: 25800 | 166200 | 27700
Station Service Office | [13 empty] | 0 | 0
Fuel Tanks SS | [13 empty] | 0 | 0
Switch Yard SS |  | 7: 159360; 8: 161120; 9: 156480; 10: 168000; 12: 152640; 12: 157760 | 955360 | 159226.6667
[14 empty] | 0 | 0
[14 empty] | 0 | 0
TOTAL OTHERS |  | 7: 184800; 8: 192800; 9: 186120; 10: 195480; 12: 178800; 12: 183560 | 1121560 | 186926.6667
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
SwitchGear Bkr1 SS |  | 7: 1126712.5; 8: 1097708.5; 9: 1046123; 10: 1076282.5; 12: 1059253; 12: 1087062.87 | 6493142.37 | 1082190.395
SwitchGear Bkr3 SS |  | 7: 301288.25; 8: 306636; 9: 302425.25; 10: 302817.5; 12: 284381.05; 12: 317414.7 | 1814962.75 | 302493.7917
[14 empty] | 0 | 0
Total |  | 7: 1428000.75; 8: 1404344.5; 9: 1348548.25; 10: 1379100; 12: 1343634.05; 12: 1404477.57 | 8308105.12 | 1384684.1867
Total SS from GAC |  | 7: 9840; 8: 4080; 9: 1740; 10: 2040; 12: 1800; 12: 2040 | 21540 | 3590
Total Station Service Power |  | 7: 1327559; 8: 1300776; 9: 1218598; 10: 1273462; 12: 1240045.62; 12: 1298845 | 7659285.62 | 1276547.6033
Total Unit #11 SS (Not Plant) | [13 empty] | 0 | 0
Total Unit #10 SS (Not Plant) | [13 empty] | 0 | 0
[14 empty] | 0 | 0
TOTAL STATION POWER |  | 7: 1786153; 8: 1778088; 9: 1613890; 10: 1721624; 12: 1667240.62; 12: 1758801 | 10325796.62 | 1720966.1033
KWH | [13 empty] | 0
ENERGY DISTRIBUTION | [13 empty] | 0
0
0
0
0
GROSS ENERGY DISTRIBUTION | [13 empty] | 0
Gross Electric Energy Produced |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
Gross Energy Used in Water Plants |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
PLANT TOTAL GROSS ENERGY USED |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
0
NET ENERGY DISTRIBUTION | [13 empty] | 0
Net Electricity to Distribution |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
Net Energy used on water to distribution |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
PLANT TOTAL NET ENERGY USED |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
0
Plant Service / Gross Output |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
0
BTU's | [13 empty] | 0
Fuel No. 2 Consumed (BTU's) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
Fuel No. 6 Consumed (BTU's) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
TOTAL ENERGY IN FUEL |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
0
GROSS ENERGY DISTRIBUTION | [13 empty] | 0
Gross Electric Energy Produced |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
Gross Energy Used in Water Plants |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
PLANT TOTAL GROSS ENERGY USED |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
0
NET ENERGY DISTRIBUTION | [13 empty] | 0
Net Electricity to Distribution |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
Net Energy used on water to distribution |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
PLANT TOTAL NET ENERGY USED |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
0
Plant Service / NET Output |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
0
EFFICIENCY | [13 empty] | 0
0
Gross Efficiency | [13 empty] | 0
Electric Generating Plant Only |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
Water Desalination Plant only |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
Combined Generating and Water Plant |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
0
Net Efficiency | [13 empty] | 0
Electric Generating Plant Only |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
Water Desalination Plant only |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
Combined Generating and Water Plant |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
0
Heat Rates BTU/KWH | [13 empty] | 0
0
Gross Heat Rate | [13 empty] | 0
Electric Generating Plant Only |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
Water Desalination Plant only |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
Combined Generating and Water Plant |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
0
Net Heat Rate | [13 empty] | 0
Electric Generating Plant Only |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
Water Desalination Plant only |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
Combined Generating and Water Plant |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
[14 empty] | 0 | 0
pag4 | [13 empty] | 0 | 0
Desalination Plants Summary | [13 empty] | 0 | 0
Unit Service HRS | [13 empty] | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit Output GALS | [13 empty] | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
From TC |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
RO WAPA Meter |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
RO 7Seas water Meter 1 |  | 7: 37516000; 8: 39683000; 9: 32676000; 10: 37374000; 12: 36186000; 12: 38640000 | 222075000 | 37012500
RO 7Seas water Meter 2 |  | 7: 37390000; 8: 39542000; 9: 32563000; 10: 37249000; 12: 36082000; 12: 38582000 | 221408000 | 36901333.3333
RO Meter Average |  | 7: 37453000; 8: 39612500; 9: 32619500; 10: 37311500; 12: 36134000; 12: 38611000 | 221741500 | 36956916.6667
RO 7Seas ANNEXwater Meter 1 |  | 7: 53489000; 8: 49507000; 9: 50040000; 10: 50630000; 12: 51000000; 12: 50089000
RO 7Seas ANNEX water Meter 2 |  | 7: 53630000; 8: 49527000; 9: 50154000; 10: 50942000; 12: 51229000; 12: 50195000
RO 7Seas ANNEX water Meter 3 |  | 7: 53484000; 8: 49494000; 9: 50066000; 10: 50643000; 12: 51105000; 12: 50095000
RO Meter Average |  | 7: 53534333.3333; 8: 49509333.3333; 9: 50086666.6667; 10: 50738333.3333; 12: 51111333.3333; 12: 50126333.3333 | 305106333.3333 | 50851055.5556
STX TOTALS |  | 7: 90987333.3333; 8: 89121833.3333; 9: 82706166.6667; 10: 88049833.3333; 12: 87245333.3333; 12: 88737333.3333 | 526847833.3333 | 87807972.2222
Unit Cond LBS | [13 empty] | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
STX TOTALS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit LP Steam LBS | [13 empty] | 0 | 0
[14 empty] | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
STX TOTALS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit HP Steam LBS | [13 empty] | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
STT TOTALS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit Utilization Factor Percent | [13 empty] | 0% | 0%
IDE 3 | [13 empty] | 0% | 0% | bar: 7 to 12
IDE 4 | [13 empty] | 0% | 0% | bar: 7 to 12
IDE 5 | [13 empty] | 0% | 0% | bar: 7 to 12
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0% | 0%
Boilers Summary | [13 empty] | 0 | 0
Service Hrs | [13 empty] | 0 | 0
WHB 21 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
HRSG 24 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Boiler 11 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
This Month Gals | [13 empty] | 0 | 0
WHB 21 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
HRSG 24 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Boiler 11 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
TOTALS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
This Month LP STM LBS | [13 empty] | 0 | 0
WHB 21 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
HRSG 24 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Boiler 11 | [13 empty] | 0 | 0
TOTALS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
This Month HP STM LBS | [13 empty] | 0 | 0
WHB 21 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
HRSG 24 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0
Boiler 11 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
TOTALS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Water Distribution | [13 empty] | 0 | 0
Total Water Produced |  | 7: 90987333.3333; 8: 89121833.3333; 9: 82706166.6667; 10: 88049833.3333; 12: 87245333.3333; 12: 88737333.3333 | 526847833.3333 | 87807972.2222
Total to Distribution Tank |  | 7: 89206406.6667; 8: 87271346.6667; 9: 81464380; 10: 86830084.6667; 12: 85733049.6667; 12: 87158109.6667 | 517663377.3333 | 86277229.5556
Apparent Station Use |  | 7: 1780926.6667; 8: 1850486.6667; 9: 1241786.6667; 10: 1219748.6667; 12: 1512283.6667; 12: 1579223.6667 | 9184456 | 1530742.6667
Water to day Tank (Booster) Plus UPW Product |  | 7: 1151333.3333; 8: 1244333.3333; 9: 1259000; 10: 1001333.3333; 12: 907333.3333; 12: 983333.3333 | 6546666.6667 | 1091111.1111
Water to the Demineralizer(regen) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Boilers Make Up |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 16 Noxwater |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 17 Noxwater |  | 7: 8237911.2549; 8: 813283.4473; 9: 756803.4668; 10: 825476.5625; 12: 760796.3867; 12: 4178241.6992 | 15572512.8174 | 2595418.8029
Unit 19 Noxwater |  | 7: 136276.123; 8: 214627.1973; 9: 360488.5254; 10: 39235.8398; 12: 57672.3633; 12: 27504.3945 | 835804.4434 | 139300.7406
Unit 20 Noxwater |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 15998.0469 | 15998.0469 | 15998.0469
Total Wtr to NOX |  | 7: 1007500; 8: 1094100; 9: 1093700; 10: 849900; 12: 812300; 12: 873400 | 5730900 | 955150
Station Wtr Warehouse & Eng. |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Plant Service Water |  | 7: 26900; 8: 17300; 9: 20400; 10: 50600; 12: 26700; 12: 20800 | 162700 | 27116.6667
Admin. Off. Water |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
WTR to Fire Hydrants |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Total Water Used |  | 7: 1780926.6667; 8: 1850486.6667; 9: 1241786.6667; 10: 1219748.6667; 12: 1512283.6667; 12: 1579223.6667 | 9184456 | 1530742.6667
Unaccountable Water |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Steam Summary | [13 empty] | 0 | 0
LP Steam LBS | [13 empty] | 0 | 0
Total Steam Produced |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
From Steam Turbine 10 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
From Steam Turbine 11 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
[14 empty] | 0 | 0
HP STM to IDE's Ejectors | [13 empty] | 0 | 0
LP STM to IDE's Process |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Used Steam for Production |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
[14 empty] | 0 | 0
Others uses & Deareator |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
HP Steam LBS | [13 empty] | 0 | 0
Total Steam Produced |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
To Steam Turbine 10 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
To Steam Turbine 11 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
From Steam Turbines |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
HP STM to IDE's Ejectors |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
LP STM to IDE's Process | [13 empty] | 0 | 0
Used Steam for Production |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
[14 empty] | 0 | 0
Others uses & Deareator |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Boiler MUF from MUF Meters |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Boiler MUF from Desal Unit HPSTM Meters |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Boilers MUF per Desal Design Quantities |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
LPSTM to Desal/Condensate Return | [13 empty] | 0% | 0% | bar: 7 to 12
Boiler 10 MUF/HPSTM Generated | [13 empty] | 0% | 0%
Boiler 11 MUF/HPSTM Generated |  | 7: N/A; 8: N/A; 9: N/A; 10: N/A; 12: N/A; 12: N/A | 0% | 0%
WHB MUF / HP & LPSTM Generated |  | 7: N/A; 8: N/A; 9: N/A; 10: N/A; 12: N/A; 12: N/A | 0 | 0
[14 empty] | 0% | 0%
pag5 | [13 empty] | 0% | 0%
Feeder KWH | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 7: 1360494.62; 8: 1358974.88; 9: 1203228; 10: 1236634; 12: 1144082; 12: 1184869.5 | 7488283 | 1248047.1667
Feeder # 2 (13 Kv) |  | 7: 3241831.56; 8: 3157129.75; 9: 2883075; 10: 2859160.25; 12: 2675297.25; 12: 2639121 | 17455614.81 | 2909269.135
Feeder # 3 (13(Kv) |  | 7: 1111674; 8: 1126770; 9: 1084143; 10: 1086359; 12: 969113; 12: 1013913 | 6391972 | 1065328.6667
Feeder # 4 (13 Kv) |  | 7: 1542316.75; 8: 1558387; 9: 1484825; 10: 1499464.5; 12: 1392114.5; 12: 1357023.75 | 8834131.5 | 1472355.25
Feeder # 5 (13 Kv) |  | 7: 3890000; 8: 3720000; 9: 3630000; 10: 3620000; 12: 3230000; 12: 3090000 | 21180000 | 3530000
Feeder # 6 (13 Kv) |  | 7: 2272777; 8: 2244390; 9: 2070676; 10: 2085241; 12: 1905874; 12: 1980862 | 12559820 | 2093303.3333
Feeder # 9A (13 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 6B (24 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 8 (24 Kv) |  | 7: 4999139.5; 8: 5863816.5; 9: 6954336; 10: 7030357; 12: 5578868; 12: 4475879 | 34902396 | 5817066
Feeder # 9B (24Kv) |  | 7: 4274225.25; 8: 2607787.671; 9: 0; 10: 0; 12: 1139488.6; 12: 1813588.4 | 9835089.921 | 2458772.4803
Feeder # 10A (24 Kv) |  | 7: 0; 8: 832165; 9: 1843955; 10: 1859330; 12: 1776401; 12: 1880437 | 8192288 | 1638457.6
Feeder # 10 (24 Kv) |  | 7: 1532181; 8: 1548799.5; 9: 1485914.75; 10: 1507122.75; 12: 1467690.5; 12: 1404689.5 | 8946398 | 1491066.3333
TOTALS |  | 7: 24224639.68; 8: 24018220.301; 9: 22640152.75; 10: 22783668.5; 12: 21278928.85; 12: 20840383.15 | 135785993.231 | 22630998.8718
Feeder Planned Outages | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 2 (13 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 3 (13(Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 4 (13 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 5 (13 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 6 (13 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 6B (24 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0
Feeder # 8 (24 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 9 (24Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 10 (24 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
TOTALS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder Forced Outages | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 7: 1; 8: 2; 9: 4; 10: 1; 12: 0; 12: 0 | 8 | 2
Feeder # 2 (13 Kv) |  | 7: 9; 8: 2; 9: 7; 10: 4; 12: 4; 12: 1 | 27 | 4.5
Feeder # 3 (13(Kv) |  | 7: 1; 8: 3; 9: 5; 10: 3; 12: 3; 12: 1 | 16 | 2.6667
Feeder # 4 (13 Kv) |  | 7: 1; 8: 3; 9: 5; 10: 2; 12: 2; 12: 1 | 14 | 2.3333
Feeder # 5 (13 Kv) |  | 7: 1; 8: 2; 9: 2; 10: 1; 12: 0; 12: 0 | 6 | 1.5
Feeder # 6 (13 Kv) |  | 7: 1; 8: 1; 9: 5; 10: 1; 12: 0; 12: 1 | 9 | 1.8
Feeder # 6B (24 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0
Feeder # 8 (24 Kv) |  | 7: 4; 8: 1; 9: 1; 10: 1; 12: 0; 12: 1 | 8 | 1.6
Feeder # 9 (24Kv) |  | 7: 2; 8: 1; 9: 0; 10: 0; 12: 0; 12: 2 | 5 | 1.6667
Feeder # 10 (24 Kv) |  | 7: 0; 8: 4; 9: 11; 10: 2; 12: 8; 12: 1 | 26 | 5.2
TOTALS |  | 7: 20; 8: 19; 9: 40; 10: 15; 12: 17; 12: 8 | 119 | 19.8333
Feeder Total Outages HRS | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 7: 0.41667; 8: 2.25; 9: 1.5833; 10: 1.9; 12: 0; 12: 0 | 6.15 | 1.5375
Feeder # 2 (13 Kv) |  | 7: 1.75; 8: 15.9167; 9: 3.45; 10: 2.9833; 12: 1.3667; 12: 0.083333 | 25.55 | 4.2583
Feeder # 3 (13(Kv) |  | 7: 0.43333; 8: 4.35; 9: 2.85; 10: 0.53333; 12: 1.2167; 12: 0.033333 | 9.4167 | 1.5694
Feeder # 4 (13 Kv) |  | 7: 0.81667; 8: 3.0167; 9: 3.1833; 10: 2.3333; 12: 1.2167; 12: 0.083333 | 10.65 | 1.775
Feeder # 5 (13 Kv) |  | 7: 0.41667; 8: 2.2333; 9: 0.81667; 10: 0.033333; 12: 0; 12: 0 | 3.5 | 0.875
Feeder # 6 (13 Kv) |  | 7: 0.83333; 8: 2.8167; 9: 3.05; 10: 1.9; 12: 0; 12: 0.1 | 8.7 | 1.74
Feeder # 6B (24 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0
Feeder # 8 (24 Kv) |  | 7: 1.3833; 8: 2.2833; 9: 0.73333; 10: 0.033333; 12: 0; 12: 0.083333 | 4.5167 | 0.90333
Feeder # 9 (24Kv) |  | 7: 2.1; 8: 2.8333; 9: 0; 10: 0; 12: 0; 12: 0.2 | 5.1333 | 1.7111
Feeder # 10 (24 Kv) |  | 7: 0; 8: 6.5667; 9: 3.9167; 10: 2.1833; 12: 1.75; 12: 0.033333 | 14.45 | 2.89
Feeder loss sales KWH | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 7: 762.3527; 8: 4122.2696; 9: 2651.819; 10: 3166.1563; 12: 0; 12: 0 | 10702.5977 | 2675.6494
Feeder # 2 (13 Kv) |  | 7: 7643.2539; 8: 69018.1735; 9: 13881.2487; 10: 11510.9801; 12: 5087.7679; 12: 295.6336 | 107437.0577 | 17906.1763
Feeder # 3 (13(Kv) |  | 7: 647.8577; 8: 6626.7147; 9: 4308.4537; 10: 779.3106; 12: 1640.3935; 12: 45.4282 | 14048.1584 | 2341.3597
Feeder # 4 (13 Kv) |  | 7: 1694.8156; 8: 6344.4532; 9: 6594.0053; 10: 4717.4164; 12: 2356.3976; 12: 152.0134 | 21859.1015 | 3643.1836
Feeder # 5 (13 Kv) |  | 7: 2179.7602; 8: 11200.2876; 9: 4122.0366; 10: 162.1936; 12: 0; 12: 0 | 17664.278 | 4416.0695
Feeder # 6 (13 Kv) |  | 7: 2548.5277; 8: 8529.1968; 9: 8808.9292; 10: 5338.8464; 12: 0; 12: 266.2807 | 25491.7808 | 5098.3562
Feeder # 6B (24 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0
Feeder # 8 (24 Kv) |  | 7: 9312.3096; 8: 18051.4316; 9: 7090.3416; 10: 314.9943; 12: 0; 12: 501.3867 | 35270.4638 | 7054.0928
Feeder # 9 (24Kv) |  | 7: 12098.4944; 8: 9969.0556; 9: 0; 10: 0; 12: 0; 12: 487.6549 | 22555.2049 | 7518.4016
Feeder # 10 (24 Kv) |  | 7: 0; 8: 13791.6875; 9: 8127.3121; 10: 4435.8013; 12: 3575.995; 12: 62.9369 | 29993.7328 | 5998.7466
TOTALS |  | 7: 36887.3718; 8: 147653.2701; 9: 55584.1463; 10: 30425.699; 12: 12660.5539; 12: 1811.3344 | 285022.3755 | 47503.7292
Plant Feeder Total Planned Outages | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 2 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 3 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 4 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 5 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 6 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 9 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 10 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
TOTALS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Plant Feeder Total Forced Outages | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 0; 8: 2; 9: 4; 10: 0; 12: 0; 12: 0 | 6 | 3
Feeder # 2 |  | 7: 9; 8: 2; 9: 7; 10: 4; 12: 4; 12: 0 | 26 | 5.2
Feeder # 3 |  | 7: 0; 8: 3; 9: 5; 10: 3; 12: 3; 12: 0 | 14 | 3.5
Feeder # 4 |  | 7: 0; 8: 3; 9: 5; 10: 2; 12: 2; 12: 0 | 12 | 3
Feeder # 5 |  | 7: 0; 8: 2; 9: 2; 10: 0; 12: 0; 12: 0 | 4 | 2
Feeder # 6 |  | 7: 0; 8: 0; 9: 5; 10: 0; 12: 0; 12: 0 | 5 | 5
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 4; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 4 | 4
Feeder # 9 |  | 7: 2; 8: 0; 9: 0; 10: 0; 12: 0; 12: 2 | 4 | 2
Feeder # 10 |  | 7: 0; 8: 4; 9: 11; 10: 2; 12: 8; 12: 0 | 25 | 6.25
TOTALS |  | 7: 15; 8: 16; 9: 39; 10: 11; 12: 17; 12: 2 | 100 | 16.6667
Plant Feeder Total Outages Time | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 0.41667; 8: 2.25; 9: 1.5833; 10: 1.9; 12: 0; 12: 0 | 6.15 | 1.5375
Feeder # 2 |  | 7: 1.75; 8: 15.9167; 9: 3.45; 10: 2.9833; 12: 1.3667; 12: 0.083333 | 25.55 | 4.2583
Feeder # 3 |  | 7: 0.43333; 8: 4.35; 9: 2.85; 10: 0.53333; 12: 1.2167; 12: 0.033333 | 9.4167 | 1.5694
Feeder # 4 |  | 7: 0.81667; 8: 3.0167; 9: 3.1833; 10: 2.3333; 12: 1.2167; 12: 0.083333 | 10.65 | 1.775
Feeder # 5 |  | 7: 0.41667; 8: 2.2333; 9: 0.81667; 10: 0.033333; 12: 0; 12: 0 | 3.5 | 0.875
Feeder # 6 |  | 7: 0.83333; 8: 2.8167; 9: 3.05; 10: 1.9; 12: 0; 12: 0.1 | 8.7 | 1.74
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 1.3833; 8: 2.2833; 9: 0.73333; 10: 0.033333; 12: 0; 12: 0.083333 | 4.5167 | 0.90333
Feeder # 9 |  | 7: 2.1; 8: 2.8333; 9: 0; 10: 0; 12: 0; 12: 0.2 | 5.1333 | 1.7111
Feeder # 10 |  | 7: 0; 8: 6.5667; 9: 3.9167; 10: 2.1833; 12: 1.75; 12: 0.033333 | 14.45 | 2.89
TOTALS | [13 empty] | 0 | 0
Plant Feeder Total Loss sales | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 762.3527; 8: 4122.2696; 9: 2651.819; 10: 3166.1563; 12: 0; 12: 0 | 10702.5977 | 2675.6494
Feeder # 2 |  | 7: 7643.2539; 8: 69018.1735; 9: 13881.2487; 10: 11510.9801; 12: 5087.7679; 12: 295.6336 | 107437.0577 | 17906.1763
Feeder # 3 |  | 7: 647.8577; 8: 6626.7147; 9: 4308.4537; 10: 779.3106; 12: 1640.3935; 12: 45.4282 | 14048.1584 | 2341.3597
Feeder # 4 |  | 7: 1694.8156; 8: 6344.4532; 9: 6594.0053; 10: 4717.4164; 12: 2356.3976; 12: 152.0134 | 21859.1015 | 3643.1836
Feeder # 5 |  | 7: 2179.7602; 8: 11200.2876; 9: 4122.0366; 10: 162.1936; 12: 0; 12: 0 | 17664.278 | 4416.0695
Feeder # 6 |  | 7: 2548.5277; 8: 8529.1968; 9: 8808.9292; 10: 5338.8464; 12: 0; 12: 266.2807 | 25491.7808 | 5098.3562
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 9312.3096; 8: 18051.4316; 9: 7090.3416; 10: 314.9943; 12: 0; 12: 501.3867 | 35270.4638 | 7054.0928
Feeder # 9 |  | 7: 12098.4944; 8: 9969.0556; 9: 0; 10: 0; 12: 0; 12: 487.6549 | 22555.2049 | 7518.4016
Feeder # 10 |  | 7: 0; 8: 13791.6875; 9: 8127.3121; 10: 4435.8013; 12: 3575.995; 12: 62.9369 | 29993.7328 | 5998.7466
TOTALS |  | 7: 36887.3718; 8: 147653.2701; 9: 55584.1463; 10: 30425.699; 12: 12660.5539; 12: 1811.3344 | 285022.3755 | 47503.7292
Line Feeder Total Planned Outages | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 2 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 3 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 4 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 5 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 6 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 9 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 10 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
TOTALS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Line Feeder Total Forced Outages | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 1; 8: 0; 9: 0; 10: 1; 12: 0; 12: 0 | 2 | 1
Feeder # 2 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 1 | 1 | 1
Feeder # 3 |  | 7: 1; 8: 0; 9: 0; 10: 0; 12: 0; 12: 1 | 2 | 1
Feeder # 4 |  | 7: 1; 8: 0; 9: 0; 10: 0; 12: 0; 12: 1 | 2 | 1
Feeder # 5 |  | 7: 1; 8: 0; 9: 0; 10: 1; 12: 0; 12: 0 | 2 | 1
Feeder # 6 |  | 7: 1; 8: 1; 9: 0; 10: 1; 12: 0; 12: 1 | 4 | 1
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 0; 8: 1; 9: 1; 10: 1; 12: 0; 12: 1 | 4 | 1
Feeder # 9 |  | 7: 0; 8: 1; 9: 0; 10: 0; 12: 0; 12: 0 | 1 | 1
Feeder # 10 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 1 | 1 | 1
TOTALS |  | 7: 5; 8: 3; 9: 1; 10: 4; 12: 0; 12: 6 | 19 | 3.8
Line Feeder Total Outages Time | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 2 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 3 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 4 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 5 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 6 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 9 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 10 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
TOTALS | [13 empty] | 0 | 0
Line Feeder Total Loss sales | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 2 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 3 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 4 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 5 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 6 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 9 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Feeder # 10 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
TOTALS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
pag6 | [13 empty] | 0 | 0
Units Outages | [13 empty] | 0 | 0
Unit 10 ST | [13 empty] | 6 | 1 | bar: 7 to 12
Unit 11 ST | [13 empty] | 6 | 1 | bar: 7 to 12
Unit 11 BLR | [13 empty] | 6 | 1 | bar: 7 to 12
Unit 16 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 17 |  | 7: 1; 8: 1; 9: 2; 10: 0; 12: 0; 12: 0 | 4 | 1.3333
Unit 19 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 20 | [13 empty] | 6 | 1 | bar: 7 to 12
Aggreko |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
HRSG 21 | [13 empty] | 6 | 1 | bar: 7 to 12
HRSG 24 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0
Units Outages Duration | [13 empty] | 0 | 0
Unit 10 ST |  | 7: 744; 8: 744; 9: 720; 10: 744; 12: 720; 12: 744 | 4416 | 736
Unit 11 ST |  | 7: 744; 8: 744; 9: 720; 10: 744; 12: 720; 12: 744 | 4416 | 736
Unit 11 BLR |  | 7: 744; 8: 744; 9: 720; 10: 744; 12: 720; 12: 744 | 4416 | 736
Unit 16 |  | 7: 744; 8: 744; 9: 720; 10: 744; 12: 720; 12: 744 | 4416 | 736
Unit 17 |  | 7: 0; 8: 0; 9: 26.65; 10: 0; 12: 0; 12: 0 | 26.65 | 26.65
Unit 19 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 20 |  | 7: 744; 8: 744; 9: 720; 10: 744; 12: 720; 12: 723.3167 | 4395.3167 | 732.5528
Aggreko |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
HRSG 21 |  | 7: 744; 8: 744; 9: 720; 10: 744; 12: 720; 12: 744 | 4416 | 736
HRSG 24 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit Planned Outages | [13 empty] | 0 | 0
Unit 10 ST | [13 empty] | 6 | 1 | bar: 7 to 12
Unit 11 ST | [13 empty] | 6 | 1 | bar: 7 to 12
Unit 11 BLR | [13 empty] | 6 | 1 | bar: 7 to 12
Unit 16 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 17 |  | 7: 1; 8: 1; 9: 0; 10: 0; 12: 0; 12: 0 | 2 | 1
Unit 19 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 20 | [13 empty] | 6 | 1 | bar: 7 to 12
Aggreko |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
HRSG 21 | [13 empty] | 6 | 1 | bar: 7 to 12
HRSG 24 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0
Unit Planned Outages Duration | [13 empty] | 0 | 0
Unit 10 ST |  | 7: 744; 8: 744; 9: 720; 10: 744; 12: 720; 12: 744 | 4416 | 736
Unit 11 ST |  | 7: 744; 8: 744; 9: 720; 10: 744; 12: 720; 12: 744 | 4416 | 736
Unit 11 BLR |  | 7: 744; 8: 744; 9: 720; 10: 744; 12: 720; 12: 744 | 4416 | 736
Unit 16 |  | 7: 744; 8: 744; 9: 720; 10: 744; 12: 720; 12: 744 | 4416 | 736
Unit 17 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 19 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 20 |  | 7: 744; 8: 744; 9: 720; 10: 744; 12: 720; 12: 723.3167 | 4395.3167 | 732.5528
Aggreko |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
HRSG 21 |  | 7: 744; 8: 744; 9: 720; 10: 744; 12: 720; 12: 744 | 4416 | 736
HRSG 24 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0
Unit Forced Outages |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 10 ST |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 11 ST |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 11 BLR |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 16 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 17 |  | 7: 0; 8: 0; 9: 2; 10: 0; 12: 0; 12: 0 | 2 | 2
Unit 19 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 20 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Aggreko |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
HRSG 21 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
HRSG 24 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0
Unit Forced Outages Duration |  | 7: 0; 8: 0; 9: 2; 10: 0; 12: 0; 12: 0 | 2 | 2
Unit 10 ST |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 11 ST |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 11 BLR |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 16 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 17 |  | 7: 0; 8: 0; 9: 26.65; 10: 0; 12: 0; 12: 0 | 26.65 | 26.65
Unit 19 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 20 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Aggreko |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
HRSG 21 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
HRSG 24 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0
Plant Power Distribution | [13 empty] | 0 | 0
Total 13KV Feeders |  | 7: 13419093.93; 8: 13165651.63; 9: 12355947; 10: 12386858.75; 12: 11316480.75; 12: 11265789.25 | 73909821.31 | 12318303.5517
Total 24KV Feeders |  | 7: 10805545.75; 8: 10852568.671; 9: 10284205.75; 10: 10396809.75; 12: 9962448.1; 12: 9574593.9 | 61876171.921 | 10312695.3202
Feeder Totals |  | 7: 24224639.68; 8: 24018220.301; 9: 22640152.75; 10: 22783668.5; 12: 21278928.85; 12: 20840383.15 | 135785993.231 | 22630998.8718
Total Generation |  | 7: 25719989.5; 8: 25797063.5; 9: 24243512.5; 10: 24404586; 12: 22938640; 12: 22207306.406 | 145311097.906 | 24218516.3177
24 KV BUS at XFMR-1 (T1) |  | 7: 66909.75; 8: 391221.84; 9: 1276007.57; 10: 55735.12; 12: 63357.25; 12: 36349 | 1889580.53 | 314930.0883
24 KV BUS at XFMR-2 (T2) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
24 KV BUS at XFMR-3 (T3) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
XFMR T1 in |  | 7: 66510; 8: 389244; 9: 1270567; 10: 55447; 12: 62657; 12: 36161
XFMR T1 out |  | 7: 4351087; 8: 4122766; 9: 4142281; 10: 5145701; 12: 4707082; 12: 5536054
XFMR T3 in |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0
XFMR T3 out |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0
XFMR T4in (from #16) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0
XFMR T4 out ( |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0
XFMR T5 in (from #20) |  | 7: 0; 8: 99999416; 9: 584; 10: 0; 12: 0; 12: 81566
XFMR T5 out |  | 7: 5558411; 8: 5172388; 9: 4438906; 10: 4536047; 12: 4221366; 12: 3120464
T1 &T3&T4 & T5 Available |  | 7: 9976008; 8: 109683814; 9: 9852338; 10: 9737195; 12: 8991105; 12: 8774245 | 157014705 | 26169117.5
T1 &T3 & T4 & T5 Losses |  | 7: 47669.07; 8: 366338.699; 9: 251331.5; 10: 237737.5; 12: 312477.1; 12: 41634.314 | 1257188.183 | 209531.3638
Net Distributed |  | 7: 25672320.43; 8: 25430724.801; 9: 23992181; 10: 24166848.5; 12: 22626162.9; 12: 22165672.092 | 144053909.723 | 24008984.9538
Line Department |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Water Department |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Power Plant Services |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Administration & General |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Plant Station Service |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Net Available from Bus |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Wapa KWH From Dist |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
SwitchGear Bkr1 SS |  | 7: 1126712.5; 8: 1097708.5; 9: 1046123; 10: 1076282.5; 12: 1059253; 12: 1087062.87 | 6493142.37 | 1082190.395
SwitchGear Bkr3 SS |  | 7: 301288.25; 8: 306636; 9: 302425.25; 10: 302817.5; 12: 284381.05; 12: 317414.7 | 1814962.75 | 302493.7917
Total Station Service Power |  | 7: 1437840.75; 8: 1408424.5; 9: 1350288.25; 10: 1381140; 12: 1345434.05; 12: 1406517.57 | 8329645.12 | 1388274.1867
Net KWH Available for Sale |  | 7: 24234479.68; 8: 24022300.301; 9: 22641892.75; 10: 22785708.5; 12: 21280728.85; 12: 20759154.522 | 135724264.603 | 22620710.7672
Plant Unaccountable |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: -83268.628
Peak Load: |  | 7: 41080; 8: 41790; 9: 40070; 10: 39340; 12: 39400; 12: 37330 | 239010 | 39835
Day |  | 7: Thursday; 8: Sunday; 9: Tuesday; 10: Saturday; 12: Sunday; 12: Friday |  | 0
Date |  | 7: 2020-07-02; 8: 2020-08-16; 9: 2020-09-29; 10: 2020-10-10; 12: 2020-11-08; 12: 2021-12-17
Hour |  | 7: 19:20; 8: 19:21; 9: 19:00; 10: 18:39; 12: 19:00; 12: 18:00
Min Load |  | 7: 27650; 8: 26320; 9: 25710; 10: 25910; 12: 24450; 12: 23490 | 153530 | 25588.3333
Day |  | 7: Sunday; 8: Wednesday; 9: Sunday; 10: Thursday; 12: Sunday; 12: Tuesday
Date |  | 7: 2020-07-19; 8: 2020-08-05; 9: 2020-09-20; 10: 2020-10-29; 12: 2020-11-29; 12: 2021-12-07
Hour |  | 7: 6:00; 8: 6:00; 9: 4:00; 10: 3:00; 12: 7:00; 12: 4:00 |  | 5:00
Pag 7
No 6 Fuel For Power |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
No 6 Fuel For Water |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
No 2 Fuel For Power |  | 7: 5520.1249; 8: 9234.3241; 9: 16758.6572; 10: 1935.0103; 12: 2188.4473; 12: 2056.614 | 37693.1779 | 6282.1963
No 2 Fuel For Water |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
O&M Factor for Water |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
BLR11FUEL2COST |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Firing | [13 empty] | 0 | 0
WHBSFCAE |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Power Boilers | [13 empty] | 0 | 0
[14 empty] | 0 | 0
TPBSFC | [13 empty] | 0 | 0
BLR11FUELCOST |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Combined Cycle | [13 empty] | 0 | 0
WHB, 16 & 17 | [13 empty] | 0 | 0
TGTFC | [13 empty] | 0 | 0
GEN161720FUELCOST |  | 7: 1999545.5291; 8: 1924719.682; 9: 1614411.4254; 10: 1804814.6582; 12: 1759979.7993; 12: 1922672.8562 | 11026143.9502 | 1837690.6584
Simple Cycle | [13 empty] | 0 | 0
12 & 14 & 22 | [13 empty] | 0 | 0
GEN 19FUELCOST |  | 7: 343756.9591; 8: 495210.025; 9: 787472.5538; 10: 88884.4036; 12: 129727.8244; 12: 63153.6403 | 1908205.4061 | 318034.2344
DIESEL | [13 empty] | 0 | 0
7 St. John | [13 empty] | 0 | 0
DIESEL_EMER. |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
GT Fuel Allocation | [13 empty] | 0 | 0
HP Stm from WHB | [13 empty] | 0 | 0
GTFCAE | [13 empty] | 0 | 0
WHBHPSTMCOST |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
whb Benefit | [13 empty] | 0 | 0
Equalization to Water | [13 empty] | 0 | 0
WHBBECW | [13 empty] | 0 | 0
WHBBENCOSTWTR |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Extraction Benefit | [13 empty] | 0 | 0
Equalization to Water | [13 empty] | 0 | 0
BECW | [13 empty] | 0 | 0
BENEQFCOSTWTR |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Gas Turbine | [13 empty] | 0 | 0
Power Allocation | [13 empty] | 0 | 0
GTFCA | [13 empty] | 0 | 0
GEN161720ADJFCOST |  | 7: 1999545.5291; 8: 1924719.682; 9: 1614411.4254; 10: 1804814.6582; 12: 1759979.7993; 12: 1922672.8562 | 11026143.9502 | 1837690.6584
Extraction Incremental | [13 empty] | 0 | 0
to Water | [13 empty] | 0 | 0
FCAWI | [13 empty] | 0 | 0
INCRFUELCOSTWTR |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
GT Fuel Allocation | [13 empty] | 0 | 0
LP Stm from WHB | [13 empty] | 0 | 0
WHBFCAW | [13 empty] | 0 | 0
WHBLPSTMCOST |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Electrc Power | [13 empty] | 0 | 0
Generation | [13 empty] | 0 | 0
TOTFUELCOSTPWR |  | 7: 3713314.5045; 8: 3744752.5614; 9: 3562453.9143; 10: 3315497.8093; 12: 3275251.6783; 12: 3510940.5724 | 21122211.0402 | 3520368.5067
RO Electricity cost |  | 7: 70963.9268; 8: 74207.1698; 9: 62238.2739; 10: 65426.4231; 12: 65607.1959; 12: 78474.4286 | 416917.418 | 69486.2363
UPW Electicity Cost |  | 7: 2771.5908; 8: 2670.0228; 9: 2442.0318; 10: 2235.9573; 12: 2189.1774; 12: 2534.4547 | 14843.2348 | 2473.8725
RO Annex Electricity cost |  | 7: 96033.7397; 8: 88297.0049; 9: 89701.1334; 10: 84224.1728; 12: 89743.4627; 12: 98498.9239
TOTFUELCSRWTR |  | 7: 166997.6665; 8: 162504.1747; 9: 151939.4073; 10: 149650.5959; 12: 155350.6585; 12: 176973.3525 | 963415.8553 | 160569.3092
Pag8 | [13 empty] | 0 | 0
No 2 BBLS | [13 empty] | 0 | 0
Inventory-Beginning of Month |  | 7: 39740.5629; 8: 34220.4379; 9: 57168.2338; 10: 40409.5766; 12: 38474.5663; 12: 36286.119 | 246299.4965 | 41049.9161
Received During Month |  | 7: 0; 8: 32182.12; 9: 0; 10: 0; 12: 0; 12: 0 | 32182.12 | 32182.12
Consumed During Month |  | 7: 5520.1249; 8: 9234.3241; 9: 16758.6572; 10: 1935.0103; 12: 2188.4473; 12: 2056.614 | 37693.1779 | 6282.1963
Inventory-End of Month |  | 7: 34220.4379; 8: 57168.2338; 9: 40409.5766; 10: 38474.5663; 12: 36286.119; 12: 34229.505 | 240788.4386 | 40131.4064
Calorific Value (BTU/GAL) |  | 7: 136784.2908; 8: 136999.0879; 9: 136999.0879; 10: 136999.0879; 12: 136999.0879; 12: 136999.0879 | 821779.7304 | 136963.2884
Calorific Value (BTU/GAL) |  | 7: 136784.2908; 8: 136999.0879; 9: 136999.0879; 10: 136999.0879; 12: 136999.0879; 12: 136999.0879 | 821779.7304 | 136963.2884
No 6 BBLS | [13 empty] | 0 | 0
Inventory-Beginning of Month |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Received During Month |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Consumed During Month |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Inventory-End of Month |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Calorific Value (BTU/GAL) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
PROPANE
Propane Value (BTU/Gal) |  | 7: 91735; 8: 91735; 9: 91735; 10: 91647; 12: 91647; 12: 91425
End of Month- Fuel in Tanks | [13 empty] | 0 | 0
No 2 BBLS | [13 empty] | 0 | 0
Tank 1 #2 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Tank 2 #2 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Tank 5 #2 |  | 7: 8440.91; 8: 37021.4; 9: 30852.38; 10: 28860.59; 12: 26657.03; 12: 24785.45 | 156617.76 | 26102.96
Tank 6 #2 |  | 7: 17422.64; 8: 11760.45; 9: 1141.19; 10: 1124.68; 12: 1127.88; 12: 944.64 | 33521.48 | 5586.9133
TOTAL |  | 7: 34220.44; 8: 57168.23; 9: 40409.58; 10: 38474.57; 12: 36286.12; 12: 34229.5 | 240788.44 | 40131.4067
No 6 BBLS | [13 empty] | 0 | 0
Tank 3 #2 |  | 7: 4452.57; 8: 4450.29; 9: 4453.2; 10: 4451.44; 12: 4450.51; 12: 4444.46 | 26702.47 | 4450.4117
Tank 4 #6 |  | 7: 3904.33; 8: 3936.1; 9: 3962.8; 10: 4037.85; 12: 4050.7; 12: 4054.95 | 23946.73 | 3991.1217
Tank 7 #6 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
TOTAL |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
Fuel Shipments | [13 empty] | 0 | 0
Date(1) |  | 7: 0; 8: 2020-08-19; 9: 0; 10: 0; 12: 0; 12: 0 | 2020-08-19 | 2020-08-19
No2 BBLS |  | 7: 0; 8: 32182.12; 9: 0; 10: 0; 12: 0; 12: 0 | 32182.12 | 32182.12
Date(2) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Date(3) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Date(4) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Date(5) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Date(6) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Date(7) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Date(8) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Date(9) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
TOTAL SHIPMENTS No 2 |  | 7: 0; 8: 32182.12; 9: 0; 10: 0; 12: 0; 12: 0 | 32182.12 | 32182.12
Date(1) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Date(2) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Date(3) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Date(4) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Date(5) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Date(6) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Date(7) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Date(8) |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
TOTAL SHIPMENTS No 6 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
[14 empty] | 0 | 0
Fuel Allocations Amount | [13 empty] | 0 | 0
Electric Power Generation |  | 7: 3713314.5045; 8: 3744752.5614; 9: 3562453.9143; 10: 3315497.8093; 12: 3275251.6783; 12: 3510940.5724 | 21122211.0402 | 3520368.5067
Water Production |  | 7: 166997.6665; 8: 162504.1747; 9: 151939.4073; 10: 149650.5959; 12: 155350.6585; 12: 176973.3525 | 963415.8553 | 160569.3092
Total #2 Fuel Cost |  | 7: 426605.2954; 8: 639765.748; 9: 1161061.1421; 10: 134059.983; 12: 151618.4179; 12: 142478.9617 | 2655589.548 | 442598.258
BBLS No. 6 for Power |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
BBLS No.6 for Water |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
BBLS No. 2 for Power |  | 7: 5520.1249; 8: 9234.3241; 9: 16758.6572; 10: 1935.0103; 12: 2188.4473; 12: 2056.614 | 37693.1779 | 6282.1963
BBLS No.2 for Water |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
No. 6 BBL Cost |  | 7: 71.9034; 8: 71.9034; 9: 71.9034; 10: 71.9034; 12: 71.9034; 12: 71.9034 | 431.4203 | 71.9034
No. 2 BBL Cost |  | 7: 77.2818; 8: 69.2813; 9: 69.2813; 10: 69.2813; 12: 69.2813; 12: 69.2784 | 423.6853 | 70.6142
Propane Cost per Bbl |  | 7: 38.3544; 8: 38.262; 9: 37.5354; 10: 38.1612; 12: 39.7362; 12: 43.4448
Propane Consumed
Unit 16 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0
Unit 17 |  | 7: 2098879.9746; 8: 1954076.7936; 9: 1388410.9176; 10: 1936648.7771; 12: 1837109.4026; 12: 1757927.9258 | 10973053.7913
Unit 20 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 24117.2548 | 24117.2548 | 24117.2548
Aggreko |  | 7: 1683103.0254; 8: 1632631.2064; 9: 1468624.0824; 10: 1729528.2229; 12: 1628680.5974; 12: 1645482.8194 | 9788049.9539
No. 2 Units BBLS No. 2 Consumed | [13 empty] | 0 | 0
Unit 10 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 11 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 16 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Unit 17 |  | 7: 1072.0288; 8: 2086.5049; 9: 5392.3457; 10: 652.0604; 12: 315.967; 12: 443.7555 | 9962.6624 | 1660.4437
Unit 19 |  | 7: 4448.0961; 8: 7147.8192; 9: 11366.3115; 10: 1282.9499; 12: 1872.4803; 12: 911.5919 | 27029.2488 | 4504.8748
Unit 20 |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 701.2667 | 701.2667 | 701.2667
Diesel Emergency |  | 7: 0; 8: 0; 9: 0; 10: 0; 12: 0; 12: 0 | 0 | 0
Total No. 2 Consumed |  | 7: 5520.1249; 8: 9234.3241; 9: 16758.6572; 10: 1935.0103; 12: 2188.4473; 12: 2056.614 | 37693.1779 | 6282.1963
Note on I673: Nicholson: negative

## PR-Pag1
December - 2020
Production Summary |  |  |  |  | Generating Units Heat Rate |  | FYTD | This Month
|  | FYTD | FYTD |  | (Gross Energy in KWH Produced) | This Month | AVG. | %
Item | This Month | AVG. | TOTAL | Units | Units | BTU/KWH | BTU/KWH | Efficiency
Total System Gross Generation** | 22207.3064 | 24218.5163 | 145311.0979 | MWH
Gross Power Plant Generation | 21615.68 | 23581.4417 | 141488.65 | MWH
Gross Water Production | 88737.3333 | 87807.9722 | 526847.8333 | KGAL
System Load Factor | 77.83% | 80.39% |  | % | Unit 10-Steam (10 MW) + WHBs* | N/A | N/A | N/A
Total Propane Fuel Cost | 3545434.9632 | 3238339.5579 | 19430037.3475 | $ | Unit 11-Steam (19.1 MW) + WHBs | N/A | N/A | N/A
Total No. 2 Fuel Cost | 142478.9617 | 442598.258 | 2655589.548 | $ | Unit 16-Gas Turbine (22.5 MW) | 0 | 0 | 0%
Power Fuel Cost (Internal) | 0.17061 | 0.15631 |  | $/KWH | Unit 17-Gas Turbine (21.9 MW) | 21861.11 | 20369.48 | 15.61%
Power Fuel Cost (to bus) | 0.17696 | 0.16287 |  | $/KWH | Unit 19-Gas Turbine (24.5 MW) | 24977.45 | 24176.12 | 13.66%
Water Fuel Cost (Internal) | 1.9944 | 1.8284 |  | $/KGAL | Unit 20_Gas Turbine (24.5 MW) | 41467.18 | 41467.18 | 8.23%
Water Fuel Cost (to Distribution) | 2.0305 | 1.8609 |  | $/KGAL | Aggreko (20.0 MW) | 10911.92 | 10927.17 | 31.27%
Total Power Fuel Cost | 3510940.5724 | 3520368.5067 | 21122211.0402 | $ | Total Electric Generation Only | 15044.42 | 14992.59 | 22.68%
Total Water Cost | 176973.3525 | 160569.3092 | 963415.8553 | $ | *Note:Total Electric Generation includes values of steam provided to STG #10 and #11 by HRSGs
Propane consumed | 81607.8095 | 82481.0357 | 494886.2143 | BBLS
No. 2 Fuel Consumed | 2056.614 | 6282.1963 | 37693.1779 | BBLS
[5 empty] | Power Units Availability |  | FYTD
No. 2 Fuel Received | 0 | 32182.12 | 32182.12 | BBLS |  | This Month | AVG.
[5 empty] | Unit | Percent (%) | Percent (%)
EOM No. 2 Fuel On Hand* | 17.1148 | 20.0657 |  | DAYS
Plant Water Use ( Internal | 8461.1204 | 5156.1523 | 30936.9139 | $ | Unit 10 | 0% | 0%
Plant Power Use (Internal) | 300074.1452 | 269066.091 | 1614396.5461 | $ | Unit 11 | 0% | 0%
7SEAS RO 1 Electricity Cost | 78474.4286 |  |  | $ | Unit 16 | 0% | 0%
7SEAS UPW Electricity Cost | 2534.4547 |  |  | $ | Unit 17 | 100% | 99.38%
7SEAS RO 2 Electricity Cost | 98498.9239 |  |  | $ | Unit 19 | 100% | 100%
**Note: Includes power generated by solar |  |  |  |  | Unit 20 | 2.78% | 0.46%
*Note: Based on 2000Bbl/day consumption |  |  |  |  | Aggreko | 100% | 100%
[5 empty] | HRSG 21 | 0% | 0%
[5 empty] | HRSG 24 | 100% | 100%

## PR-Pag2
December - 2020
Power Generation - Station Power |  | FYTD | TOTAL | Generating Units Average Loading |  |  | FYTD | Utilization
Item | This Month | Monthly | FYTD |  |  | This Month | AVG. | Factor
| KWH | AVG. | KWH | (KWH / Operating Hours) |  | KW | KW | Percent
Steam Turbine Generation | 0 | 0 | 0 | Unit 10 |  | 0 | 0 | 0%
Gas Turbine Generation | 21615680 | 23581441.6667 | 141488650 | Unit 11 |  | 0 | 0 | 0%
Diesel Generation | 0 | 0 | 0 | Unit 16 |  | 0 | 0 | 0%
Total Generation | 21615680 | 23581441.6667 | 141488650 | Unit 17 |  | 10267.5282 | 12385.3662 | 46.88%
Steam Station Power | 0 | 0 | 0 | Unit 19 |  | 7142.8571 | 7744.208 | 29.15%
Gas Turbine Station Power | 62750 | 45870 | 275220 | Unit 20 |  | 7677.551 | 7677.551 | 31.34%
Aggreko Station Service | 400 | 685 | 4110 | Aggreko |  | 18921.375 | 19496.0625 | 94.61%
Total Gen. Plant Station Power | 62750 | 45870 | 275220 | Diesel |  | 0 | 0 | 0%
Total Service / Gross Output | 0.2903% | 0.1959%
IPP1 | 591626.406 | 637074.651 | 3822447.906
Total System Generation | 22207306.406 | 23581441.6667 | 141488650
Generating Units Station Power
Generating Units Operating Hours |  | FYTD | TOTAL |  |  | FYTD | TOTAL | This Month | FYTD | FYTD
| This Month | Monthly | FYTD |  | This Month | AVG. | FYTD | SS Power | AVG. | SS Power
Unit | HRS | AVG. | HRS | Unit | KWH | KWH | KWH | KWH | KWH | KWH
Unit 10 | 0 | 0 | 0 | Unit 10 | 0 | 0 | 0 | 0 | 0 | 0
Unit 11 | 0 | 0 | 0 | Unit 11 | 0 | 0 | 0 | 0 | 0 | 0
Unit 16 | 0 | 0 | 0 | Unit 16 | 0 | 0 | 0 | 0 | 0 | 0
Unit 17 | 727.4 | 705.45 | 4232.7 | Unit 17 | 7468600 | 8729453.3333 | 52376720 | 2640 | 3338.3333 | 20030
Unit 19 | 29.4 | 140.0667 | 840.4 | Unit 19 | 210000 | 1141666.6667 | 6850000 | 27440 | 31586.6667 | 189520
Unit 20 | 19.6 | 19.6 | 19.6 | Unit 20 | 150480 | 150480 | 150480 | 32670 | 10945 | 65670
Aggreko | 728.6257 | 701.8496 | 4211.0976 | Aggreko | 13786600 | 13685241.6667 | 82111450 | 400 | 685 | 4110
Diesel Generation(Emergency) | 1 | 1.8 | 9 | Diesel | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | TOTAL | 21615680 | 23581441.6667 | 141488650 | 62750 | 45870 | 275220

## PR-Pag3
December - 2020
BOILERS/STM. TURBINES | SS | GAS TURBINE | SS | STX. EMERGENCY DIESEL | SS | OTHERS | SS
| Kwh |  | Kwh |  | Kwh |  | Kwh
SS10 Plant Aux. Trans 480V | 0 | Plant SS |  | Diesel | 0 | Station Service Shops | 25800
SS10 Unit Aux.. Trans 480V | 0 | Unit 16 | 0 |  |  | Station Service Office | 0
|  | Unit 17 | 600 |  |  | Fuel Tanks SS | 0
Unit 10 Total Station Power | 0 | Unit 19 | 27440 | TOTAL DIESEL | 0 | Switch Yard SS | 157760
|  | Unit 20 | 32670 |  |  | Richmond Sub SS
|  | Aggreko | 400 |  |  | Midland Sub SS
SS11 Plant Aux. Trans 480V | 0 |  |  |  |  | TOTAL OTHERS | 183560
SS11 Unit Aux.. Trans 480V | 0 | Unit SS |  | WATER PLANTS | SS
|  | Unit 16 | 0 |  | Kwh | SwitchGear Bkr1 SS | 1087062.87
Unit 11 Net Total Station Power | 0 | Unit 17 | 2040 | Plant ABC Pump usage | 0 | SwitchGear Bkr3 SS | 317414.7
|  | Unit 19 | 0 |  |  | SS10 Unit Aux Trans. | 0
|  | Unit 20 | 0 | Intake Pump A&B+Chloropac | 0 | SS11 Unit Aux Trans. | 0
HRSG 21 Station Power | 0 | TOTAL GAS TURBINES | 63150 |  |  | Total GT Unit SS | 2040
HRSG 24 Station Power** | 0 | Plant Pumps |  | RO Plant Electrical Usage | 459956
|  | Intake Pump A | 0 | UPW Electrical Usage | 14855 |  | 1406517.57
|  | Intake Pump B | 0 | RO ANNEX Electrical Usage | 577324
WHB Net Station Power | 0 | Intake Pump C | 0
TOTAL BOILERS / STM TURBINES | 0 |  |  | TOTAL WATER PLANTS | 1052135 | Total Station Service* | 1298845
*Total SS switched to a summaton of individual meters from general 'main' distribution meters summation
** No power to meter

## PR-Pag4
December - 2020
Desalination Plants Summary
|  | FYTD | TOTAL | Units Water Output
| Service | AVG. | FYTD | This Month | FYTD
Unit | HRS | HRS | HRS | GALS | GALS
RO 1 |  |  |  | 38611000 | 221741500
RO 2 |  |  |  | 50126333.3333 | 305106333.3333
STX TOTALS |  |  |  | 88737333.3333 | 526847833.3333
Boilers Summary
|  | Boilers Service Hours |  |  | Make Up Feed Water |  | Low Pressure Steam |  | High Pressure Steam
| Service | AVG. | FYTD | This Month | AVG. | FYTD | This Month | FYTD | This Month | FYTD
Unit | HRS | HRS | HRS | GALS | GALS | GALS | LBS | AVG. | LBS | AVG.
HRSG 21/IPOS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HRSG 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Boiler 11 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
TOTALS |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Distribution |  | This Month | FYTD-AVG. | FYTD |  | Steam Summary |  | LP Steam | HP Steam
|  | GALS | GALS | GALS |  | ITEM |  | LBS | LBS
Total Plant Water Produced |  | 88737333.3333 | 87807972.2222 | 526847833.3333 |  | Total Steam Produced |  | 0 | 0
Total Reverse Osmosis Produced |  | 88737333.3333 | 36956916.6667 | 221741500 |  | To Steam Turbine 10 |  |  | 0
Total to Distribution Tank |  | 87158109.6667 | 86277229.5556 | 517663377.3333 |  | To Steam Turbine 11 |  |  | 0
Apparent Station Use |  | 1579223.6667 | 1530742.6667 | 9184456 |  | From Steam Turbine 10 |  | 0 | 0
Water to day Tank |  | 983333.3333 | 1091111.1111 | 6546666.6667 |  | From Steam Turbine 11 |  | 0
UPW Feed |  | 1558423.6667 | 1503626 | 9021756
UPW Product |  | 983333.3333 | 1091111.1111 | 6546666.6667 |  | Used Steam for Production |  | 0 | 0
Water to the Demineralizer (Regen) |  | 0 | 0 | 0 |  | Others uses & Deareator |  |  | 0
Boilers Make Up |  | 0 | 0 | 0
Unit 16 Noxwater |  | 0 | 0 | 0
Unit 17 Noxwater |  | 4178241.6992 | 2595418.8029 | 15572512.8174
Unit 19 Noxwater |  | 27504.3945 | 139300.7406 | 835804.4434
Unit 20 Noxwater |  | 15998.0469 | 15998.0469 | 15998.0469
Metered Total Wtr to NOX |  | 873400 | 955150 | 5730900
Station Wtr Warehouse & Eng. |  | 0 | 0 | 0
Plant Service Water |  | 20800 | 27116.6667 | 162700
Admin. Off. Water |  | 0 | 0 | 0
WTR to Fire Hydrants |  | 0 | 0 | 0 |  | * Unaccountable value has been zeroed due to non-functional distribution
Total Water used |  | 1579223.6667 | 1530742.6667 | 9184456 |  |  | meter giving rise to high unaccountable value
Unaccountable Water |  | 0 | 0 | 0

## PR-Pag5
December - 2020
| Feeders Power Distribution |  | This Month Total Plant Outages |  |  | Month | FYTD | FYTD | Feeders Outages Summary
| Output | FYTD | Planned | Forced | Time Hrs | Lost Sales | Total | Total | Feeder | Time | Date | Reason
Feeder | KWH | AVG KWH | Outages | Outages | Duration | Kwh | Outages | Time Hrs |  | min.
[9 empty] | Feeder #9B | 6 | 2020-12-07 | Feeder opened by request of dispatch
Feeder #1A (13Kv) | 1184869.5 | 1248047.1667 | 0 | 0 | 0 | 0 | 6 | 6.15 | Feeder #3A | 2 | 2020-12-09 | Aggreko tripped off line due to loss of gas pressure
Feeder #2A (13 Kv) | 2639121 | 2909269.135 | 0 | 1 | 0.083333 | 295.6336 | 26 | 25.55 | Feeder #4A | 5 | 2020-12-09 | Aggreko tripped off line due to loss of gas pressure
Feeder #3A (13(Kv) | 1013913 | 1065328.6667 | 0 | 1 | 0.033333 | 45.4282 | 14 | 9.4167 | Feeder #6A | 6 | 2020-12-09 | Aggreko tripped off line due to loss of gas pressure
Feeder #4A (13 Kv) | 1357023.75 | 1472355.25 | 0 | 1 | 0.083333 | 152.0134 | 12 | 10.65 | Feeder #8B | 5 | 2020-12-09 | Aggreko tripped off line due to loss of gas pressure
Feeder #5A (13 Kv) | 3090000 | 3530000 | 0 | 0 | 0 | 0 | 4 | 3.5 | Feeder #9B | 6 | 2020-12-09 | Aggreko tripped off line due to loss of gas pressure
Feeder #6A (13 Kv) | 1980862 | 2093303.3333 | 0 | 1 | 0.1 | 266.2807 | 5 | 8.7 | Feeder #2A | 5 | 2020-12-12 | Unit 17 tripped due to FG-1 Vent valve position fault
Feeder #9A (13 Kv) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Feeder #10A | 2 | 2020-12-12 | Unit 17 tripped due to FG-1 Vent valve position fault
Feeder #6B (24 Kv) | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4.5167 | Feeder #10B | 4 | 2020-12-12 | Unit 17 tripped due to FG-1 Vent valve position fault
Feeder #8B (24 Kv) | 4475879 | 5817066 | 0 | 1 | 0.083333 | 501.3867 | 4 | 4.5167
Feeder #9B(24Kv) | 1813588.4 | 2458772.4803 | 0 | 2 | 0.2 | 487.6549 | 4 | 5.1333
Feeder #10A(24Kv) | 1880437 | 1638457.6 | 0 | 0 | 0 | 0 | 0 | 0
Feeder #10B(24Kv) | 1404689.5 | 1491066.3333 | 0 | 1 | 0.033333 | 62.9369 | 25 | 14.45
TOTALS | 20840383.15 | 23723665.9653 | 0 | 8 | 0.61667 | 1811.3344 | 104 | 92.5833
0
0
0
0
0

## PR-Pag6
December - 2020
Power - Water Units Outages
|  | TOTAL NUMBER OF OUTAGES |  |  |  | PLANNED OUTAGES |  |  |  | FORCED OUTAGES
| This Month | FYTD | This Month | FYTD | This Month | FYTD | Duration | FYTD | This Month | FYTD | Duration | FYTD
Unit | Outages | Outages | Hours | Hours | Outages | Outages | Hours | Hours | Outages | Outages | Hours | Hours
Unit 10ST | 1 | 6 | 744 | 4416 | 1 | 6 | 744 | 4416 | 0 | 0 | 0 | 0
Unit 11ST | 1 | 6 | 744 | 4416 | 1 | 6 | 744 | 4416 | 0 | 0 | 0 | 0
Unit11BLR | 1 | 6 | 744 | 4416 | 1 | 6 | 744 | 4416 | 0 | 0 | 0 | 0
Unit 16 | 0 | 0 | 744 | 4416 | 0 | 0 | 744 | 4416 | 0 | 0 | 0 | 0
Unit 17 | 0 | 4 | 0 | 26.65 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 26.65
Unit 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Unit 20 | 1 | 6 | 723.3167 | 4395.3167 | 1 | 6 | 723.3167 | 4395.3167 | 0 | 0 | 0 | 0
Aggreko | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HRSG 21 | 1 | 6 | 744 | 4416 | 1 | 6 | 744 | 4416 | 0 | 0 | 0 | 0
HRSG 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTALS | 5 | 34 |  |  | 5 |  |  |  | 0 | 2
Plant Power Distribution
|  |  | This Month | FYTD | FYTD |  |  |  | Peak and Min. Load Data
|  |  | KWH | KWH | AVG. | [5 empty] | FYTD
Total 13KV Feeders |  |  | 11265789.25 | 73909821.31 | 12318303.5517 |  |  |  |  | This Month | AVG.
Total 24KV Feeders |  |  | 9574593.9 | 61876171.921 | 10312695.3202 |  |  | Peak Load (KW) |  | 37330 | 39835
Feeder Totals |  |  | 20840383.15 | 135785993.231 | 22630998.8718 |  |  | Day |  | Friday
Total Generation |  |  | 22207306.406 | 145311097.906 | 24218516.3177 |  |  | Date |  | 2021-12-17
T1,T3,T4, T5, T6, T7 Available |  |  | 8774245 | 157014705 | 26169117.5 |  |  | Hour |  | 18:00
T1&T3&T4&T5&T6&T7 Losses* |  |  | 41634.314 | 1257188.183 | 209531.3638
Net Distributed |  |  | 22165672.092 | 144053909.723 | 24008984.9538 |  |  | Min. Load (KW) |  | 23490 | 25588.3333
Line Department |  |  |  | 0 | 0 |  |  | Day |  | Tuesday
Water Department |  |  |  | 0 | 0 |  |  | Date |  | 2021-12-07
Power Plant Services |  |  |  | 0 | 0 |  |  | Hour |  | 4:00
Administration & General |  |  |  | 0 | 0
Plant Station Service |  |  |  | 0 | 0
Net Available from Bus |  |  |  | 0 | 0
Wapa KWH From Dist |  |  |  | 0 | 0 |  | * meters under review
SwitchGear Bkr1 SS |  |  | 1087062.87 | 6493142.37 | 1082190.395
SwitchGear Bkr3 SS |  |  | 317414.7 | 1814962.75 | 302493.7917
Total Station Service Power |  |  | 1298845 | 8329645.12 | 1388274.1867
Net KWH Available for Sale |  |  | 20759154.522 | 135724264.603 | 22620710.7672
Plant Unaccountable |  |  | 83268.628 | 0 | 0
0
0
0
0
0

## PR-Pag7
December - 2020
|  |  | Fuel Allocation | BBLS
|  |  | Propane Fuel For Power | 81607.8095
|  |  | Propane Fuel For Water | 0
|  |  | No 2 Fuel For Power | 2056.614
|  |  | No 2 Fuel For Water | 0
|  |  | O&M Factor for Water | 0
Power Boilers
11
TPBSFC
BLR11FUELCOST
0 |  | GT Fuel Allocation
HP Stm from WHB
GTFCAE
WHBHPSTMCOST
Combined Cycle |  | 0
WHB, 16. 17. 20
TGTFC |  |  |  |  | Electrc Power
GEN1617FUELCOST |  |  |  |  | Generation
1922672.8562 |  |  |  |  | TOTFUELCOSTPWR
|  |  | Gas Turbine |  | 3510940.5724
Power Allocation
Simple Cycle |  |  | GTFCA
GEN161720ADJFCOST
GEN 19 FUELCOST |  |  | 1922672.8562
63153.6403
RO Water
DIESEL |  |  |  |  | Production Cost
Emergency Gen.
DIESEL_EMER. |  |  |  |  | 176973.3525
0
Cost Calculated at:
| 69.2784 | per BBL for No. 2
| 43.4448 | per BBL for Propane

## PR-Pag8
December - 2020
Fuel Allocations
Fuel Summary |  |  |  | ITEM | Amount | FYTD
ITEM | Propane | No2 BBLS
|  |  |  | Electric Power Generation | 3510940.5724 | 21122211.0402
Inventory-Beginning of Month |  | 36286.119 |  | Water Production* | 176973.3525 | 963415.8553
Received During Month |  | 0 |  | Total #2 Fuel Cost | 142478.9617 | 2655589.548
Consumed During Month |  | 2056.614 |  | BBLS Propane for Power | 81607.8095 | 494886.2143
Inventory-End of Month |  | 34229.505 |  | BBLS Propane for Water | 0 | 0
Calorific Value (BTU/GAL) | 91425 | 136999.0879 |  | BBLS No. 2 for Power | 2056.614 | 37693.1779
|  |  |  | BBLS No.2 for Water | 0 | 0
|  |  |  | Propane BBL Cost | 43.4448
End of Month- Fuel in Tanks |  |  |  | No. 2 BBL Cost | 69.2784
|  | No 2 BBLS |  | * Note: Includes RO Electric Usage
|  |  |  | No. 2 Oil Used | This Month | FYTD
Tank 1 |  | 0 |  | No. 2 Units | BBLS No. 2 | BBLS No. 2
Tank 2 |  | 0
Tank 3 |  | 4444.46 |  | Unit 11 | 0 | 0
Tank 4 |  | 4054.95 |  | Unit 16 | 0 | 0
Tank 5 |  | 24785.45 |  | Unit 17 | 443.7555 | 9962.6624
Tank 6 |  | 944.64 |  | Unit 19 | 911.5919 | 27029.2488
Tank 7 |  |  |  | Unit 20 | 701.2667 | 701.2667
TOTALS | 0 | 34229.505 |  | Diesel Emergency | 0 | 0
|  |  |  | Total No. 2 Consumed | 2056.614 | 37693.1779
Fuel Shipments |  |  |  | Propane Used | This Month | FYTD
|  | No2 | No2 | Propane Units | Gals | Gals
|  | Date | BBLS | Unit 16 | 0 | 0
|  |  |  | Unit 17 | 1757927.9258 | 10973053.7913
|  |  |  | Unit 20 | 24117.2548 | 24117.2548
|  |  |  | Aggreko | 1645482.8194 | 9788049.9539
|  |  |  | Total Propane Consumed | 3427528 | 20785221
TOTAL SHIPMENTS |  |  | 0
|  |  |  | Tank Fuel / Metered Fuel | Ratio
Used Oil recovered | 0 | Bbls
|  |  |  | No. 2 | 1.0443
|  |  |  | Propane | 0.98507
Ratio 0.95 to 1.05 acceptable
0
0
0
0
0

## PR-Pag9
December - 2020

## PR-Pag10
December - 2020

## PR-Pag11
December - 2020