## DataBase
FISCAL YEAR 2020-2021
|  | 31 | 31 | 30 | 31 | 30 | 31 | 31 | 28 | 31 | 30 | 31 | 0
|  | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY | JUN | FYTD | FYTD-AVG
Item | Index | 7 | 8 | 9 | 10 | 12 | 12 | 13 | 14 | 15 | 16 | 17 | 18
Total System Generation |  | 7: 25719.9895; 8: 25797.0635; 9: 24243.5125; 10: 24404.586 | 100165.1515 | 25041.2879
Gross Power Generation |  | 7: 25075.95; 8: 25132.08; 9: 23591.11; 10: 23735.79 | 97534.93 | 24383.7325
Gross Water Production |  | 7: 90987.3333; 8: 89121.8333; 9: 82706.1667; 10: 88049.8333 | 350865.1667 | 87716.2917
System Load Factor |  | 7: 82.05%; 8: 80.83%; 9: 81.77%; 10: 81.1% | 325.7% | 81.44%
Total No. 6 Fuel Cost |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Total No. 2 Fuel Cost |  | 7: 426605.2954; 8: 639765.748; 9: 1161061.1421; 10: 134059.983 | 2361492.1684 | 590373.0421
Total Propane Cost |  | 7: 3453706.8756; 8: 3267490.988; 9: 2553332.1795; 10: 3331088.4222 | 12605618.4653 | 3151404.6163
Power Fuel Cost (Internal) |  | 7: 0.15474; 8: 0.15547; 9: 0.15745; 10: 0.14599 | 0.61365 | 0.15341
Power Fuel Cost (to bus) |  | 7: 0.16018; 8: 0.16268; 9: 0.16406; 10: 0.15209 | 0.63901 | 0.15975
Water Fuel Cost (Internal) |  | 7: 1.8354; 8: 1.8234; 9: 1.8371; 10: 1.6996 | 7.1955 | 1.7989
Water Fuel Cost (to Distribution |  | 7: 1.872; 8: 1.8621; 9: 1.8651; 10: 1.7235 | 7.3227 | 1.8307
Total Power Fuel Cost |  | 7: 3713314.5045; 8: 3744752.5614; 9: 3562453.9143; 10: 3315497.8093 | 14336018.7894 | 3584004.6974
Total Water Fuel Cost |  | 7: 166997.6665; 8: 162504.1747; 9: 151939.4073; 10: 149650.5959 | 631091.8443 | 157772.9611
No. 6 Fuel Consumed |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
No. 2 Fuel Consumed |  | 7: 5520.1249; 8: 9234.3241; 9: 16758.6572; 10: 1935.0103 | 33448.1166 | 8362.0292
No. 6 Fuel Received |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
No. 2 Fuel Received |  | 7: 0; 8: 32182.12; 9: 0; 10: 0 | 32182.12 | 32182.12
EOM No. 6 Fuel On Hand |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
EOM No. 2 Fuel On Hand(based on 2000Bbl/day Consumption) |  | 7: 17.1102; 8: 28.5841; 9: 20.2048; 10: 19.2373 | 85.1364 | 21.2841
Plant Water Use ( Internal) |  | 7: 15419.311; 8: 1905.8303; 9: 2090.0527; 10: 1555.6764 | 20970.8704 | 5242.7176
Plant Power Use (Internal) |  | 7: 276393.5654; 8: 276437.3787; 9: 254105.137; 10: 251337.0171 | 1058273.0981 | 264568.2745
Heat Rates BTU/KWH | [13 empty] | 0 | 0
(Net Energy in KWH Produced) | [13 empty] | 0 | 0
Units | [13 empty] | 0 | 0
Combined Cycle-Units 10,16 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Combined Cycle-Units 11,16 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 10-Steam (10 MW) |  | 7: N/A; 8: N/A; 9: N/A; 10: N/A | 0 | 0
Unit 11-Steam (21 MW) |  | 7: N/A; 8: N/A; 9: N/A; 10: N/A | 0 | 0
Unit 16-Gas Turbine (23 MW) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 17-Gas Turbine (20.3 MW) |  | 7: 19723.3655; 8: 19377.4218; 9: 19918.1643; 10: 20433.9315 | 79452.8831 | 19863.2208
Unit 19-Gas Turbine (24 MW) |  | 7: 31163.4711; 8: 25705.1735; 9: 19292.4251; 10: 22369.8317 | 98530.9014 | 24632.7254
Unit 20_Gas Turbine (24 MW) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Aggreko |  | 7: 10887.2856; 8: 10962.7384; 9: 10998.875; 10: 10904.2078 | 43753.1068 | 10938.2767
Total Plant . |  | 7: 15100.2454; 8: 15206.0874; 9: 15197.1983; 10: 14624.6701 | 60128.2013 | 15032.0503
Desal Performance Ratios | [13 empty] | 0 | 0
IDE3 (1.25MGD) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE4 (.55MGD) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE5 (0.55MGD) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE9 (1.3MGD) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit Availability Percent | [13 empty] | 0 | 0
Unit 10 | [13 empty] | 0% | 0% | bar: 7 to 10
Unit 11 | [13 empty] | 0% | 0% | bar: 7 to 10
Unit 16 | [13 empty] | 0% | 0% | bar: 7 to 10
Unit 17 |  | 7: 100%; 8: 100%; 9: 96.3%; 10: 100% | 396.3% | 99.07%
Unit 19 |  | 7: 100%; 8: 100%; 9: 100%; 10: 100% | 400% | 100%
Unit 20 | [13 empty] | 0% | 0% | bar: 7 to 10
Aggreko |  | 7: 100%; 8: 100%; 9: 100%; 10: 100% | 400% | 100%
IDE 3 |  | 7: 100%; 8: 100%; 9: 100%; 10: 100% | 400% | 100%
IDE 4 | [13 empty] | 0% | 0% | bar: 7 to 10
IDE 5 | [13 empty] | 0% | 0% | bar: 7 to 10
IDE 9 |  | 7: 100%; 8: 100%; 9: 100%; 10: 100% | 400% | 100%
HRSG 21 | [13 empty] | 0% | 0% | bar: 7 to 10
HRSG 24 |  | 7: 100%; 8: 100%; 9: 100%; 10: 100% | 400% | 100%
Pag2 | [13 empty] | 0 | 0
Item | [13 empty] | 0 | 0
Steam Turbine Generation |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Gas Turbine Generation |  | 7: 25075950; 8: 25132080; 9: 23591110; 10: 23735790 | 97534930 | 24383732.5
Diesel Generation |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Total Generation |  | 7: 25075950; 8: 25132080; 9: 23591110; 10: 23735790 | 97534930 | 24383732.5
IPP1 |  | 7: 644039.5; 8: 664983.5; 9: 652402.5; 10: 668796 | 2630221.5 | 657555.375
Total System Generation |  | 7: 25719989.5; 8: 25797063.5; 9: 24243512.5; 10: 24404586
Steam Station Power |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Gas Turbine Station Power |  | 7: 45390; 8: 45350; 9: 49610; 10: 36910 | 177260 | 44315
Total Gen. Plant Station Power |  | 7: 45390; 8: 45350; 9: 49610; 10: 36910 | 177260 | 44315
Total Service / Gross Output |  | 7: 0.181%; 8: 0.1804%; 9: 0.2103%; 10: 0.1555% | 0.7273% | 0.1818%
Operating Hours | [13 empty] | 0 | 0
Unit 10 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 11 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 16 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 17 |  | 7: 739.5; 8: 722.8; 9: 610.5; 10: 728.2 | 2801 | 700.25
Unit 19 |  | 7: 180.1; 8: 242.4; 9: 287.9; 10: 41.9 | 752.3 | 188.075
Unit 20 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Aggreko |  | 7: 713.003; 8: 697.0245; 9: 639.6298; 10: 741.0772 | 2790.7345 | 697.6836
Diesel Generation(Emergency) |  | 7: 1; 8: 3; 9: 0; 10: 3 | 7 | 2.3333
Unit Average Loading | [13 empty] | 0 | 0
(KWH / Operating Hours) | [13 empty] | 0 | 0
Unit 10 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 11 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 16 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 17 |  | 7: 13623.1508; 8: 13655.7831; 9: 13025.7166; 10: 12180.1154 | 52484.7658 | 13121.1915
Unit 19 |  | 7: 4553.0261; 8: 6600.6601; 9: 11774.9218; 10: 7875.895 | 30804.503 | 7701.1257
Unit 20 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Aggreko |  | 7: 19890; 8: 19600; 9: 19150; 10: 19615 | 78255 | 19563.75
Diesel |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Utilization Factor | [13 empty] | 0 | 0
Unit 10 | [13 empty] | 0% | 0% | bar: 7 to 10
Unit 11 | [13 empty] | 0% | 0% | bar: 7 to 10
Unit 16 | [13 empty] | 0% | 0% | bar: 7 to 10
Unit 17 |  | 7: 62.21%; 8: 62.36%; 9: 59.48%; 10: 55.62% | 239.7% | 59.91%
Unit 19 |  | 7: 18.58%; 8: 26.94%; 9: 48.06%; 10: 32.15% | 125.7% | 31.43%
Unit 20 | [13 empty] | 0% | 0% | bar: 7 to 10
Aggreko |  | 7: 99.45%; 8: 98%; 9: 95.75%; 10: 98.08%
Diesel | 1 | [12 empty] | 0% | 0% | bar: 7 to 10
Unit Output KW | 2 | [12 empty] | 0 | 0
Unit 10 | 3 | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 11 | 4 | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 16 | 5 | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 17 | 6 | 7: 10074320; 8: 9870400; 9: 7952200; 10: 8869560 | 36766480 | 9191620
Unit 19 | 7 | 7: 820000; 8: 1600000; 9: 3390000; 10: 330000 | 6140000 | 1535000
Unit 20 | 8 | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Aggreko |  | 7: 14181630; 8: 13661680; 9: 12248910; 10: 14536230 | 54628450 | 13657112.5
Diesel |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
TOTAL | 9 | 7: 25075950; 8: 25132080; 9: 23591110; 10: 23735790 | 97534930 | 24383732.5
Unit Station Service Power | [13 empty] | 0 | 0
Unit 10 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 11 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 16 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 17 |  | 7: 2370; 8: 3560; 9: 6150; 10: 2820 | 14900 | 3725
Unit 19 |  | 7: 35520; 8: 34800; 9: 36960; 10: 27680 | 134960 | 33740
Unit 20 |  | 7: 7500; 8: 6990; 9: 6500; 10: 6410 | 27400 | 6850
Aggreko |  | 7: 260; 8: 200; 9: 2350; 10: 670 | 3480 | 870
Diesel |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
TOTAL |  | 7: 45390; 8: 45350; 9: 49610; 10: 36910 | 177260 | 44315
pag3 | [13 empty] | 0 | 0
BOILERS/STM. TURBINES | [13 empty] | 0 | 0
[14 empty] | 0 | 0
SS10 Plant Aux. Trans 480V |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
SS10 Unit Aux.. Trans 480V |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
[14 empty] | 0 | 0
Unit 10 Total Station Power |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
SS11 Plant Aux. Trans 480V |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
SS11 Unit Aux.. Trans 480V |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
[14 empty] | 0 | 0
Unit 11 Net Total Station Power |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
HRSG 21 Station Power |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
HRSG 24 Station Power |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
WHB Net Station Power |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
TOTAL BOILERS / STM TURBINES |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
GAS TURBINE | [13 empty] | 0 | 0
[14 empty] | 0 | 0
Plant SS | [13 empty] | 0 | 0
Unit 16 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 17 |  | 7: 30; 8: 980; 9: 4410; 10: 780 | 6200 | 1550
Unit 19 |  | 7: 35520; 8: 34800; 9: 36960; 10: 27680 | 134960 | 33740
Unit 20 |  | 7: 0; 8: 5490; 9: 6500; 10: 6410 | 18400 | 6133.3333
|  | 7: 260; 8: 200; 9: 2350; 10: 670 | 3480 | 870
Unit SS | [13 empty] | 0 | 0
Unit 16 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 17 |  | 7: 2340; 8: 2580; 9: 1740; 10: 2040 | 8700 | 2175
Unit 19 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 20 |  | 7: 7500; 8: 1500; 9: 0; 10: 0 | 9000 | 4500
|  | 7: 9840; 8: 4080; 9: 1740; 10: 2040 | 17700 | 4425
Plant IDE pumpage | [13 empty] | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
[14 empty] | 0 | 0
Total |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
TOTAL GAS TURBINES |  | 7: 45650; 8: 45550; 9: 51960; 10: 37580 | 180740 | 45185
STX. EMERGENCY DIESEL | [13 empty] | 0 | 0
[14 empty] | 0 | 0
Diesel |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
TOTAL DIESEL |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
WATER PLANTS | [13 empty] | 0 | 0
[14 empty] | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Intake Pump A |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Intake Pump B |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Intake Pump C |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE Intake Pumps A&B+Chloropac |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
RO Plant |  | 7: 458594; 8: 477312; 9: 395292; 10: 448162 | 1779360 | 444840
UPW Electricity |  | 7: 17911; 8: 17174; 9: 15510; 10: 15316 | 65911 | 16477.75
RO ANNEX Electricity |  | 7: 620604; 8: 567940; 9: 569716; 10: 576924 | 2335184 | 583796
TOTAL WATER PLANTS |  | 7: 1097109; 8: 1062426; 9: 980518; 10: 1040402 | 4180455 | 1045113.75
OTHERS | [13 empty] | 0 | 0
[14 empty] | 0 | 0
Station Service Shops |  | 7: 25440; 8: 31680; 9: 29640; 10: 27480 | 114240 | 28560
Station Service Office | [13 empty] | 0 | 0
Fuel Tanks SS | [13 empty] | 0 | 0
Switch Yard SS |  | 7: 159360; 8: 161120; 9: 156480; 10: 168000 | 644960 | 161240
[14 empty] | 0 | 0
[14 empty] | 0 | 0
TOTAL OTHERS |  | 7: 184800; 8: 192800; 9: 186120; 10: 195480 | 759200 | 189800
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
SwitchGear Bkr1 SS |  | 7: 1126712.5; 8: 1097708.5; 9: 1046123; 10: 1076282.5 | 4346826.5 | 1086706.625
SwitchGear Bkr3 SS |  | 7: 301288.25; 8: 306636; 9: 302425.25; 10: 302817.5 | 1213167 | 303291.75
[14 empty] | 0 | 0
Total |  | 7: 1428000.75; 8: 1404344.5; 9: 1348548.25; 10: 1379100 | 5559993.5 | 1389998.375
Total SS from GAC |  | 7: 9840; 8: 4080; 9: 1740; 10: 2040 | 17700 | 4425
Total Station Service Power |  | 7: 1327559; 8: 1300776; 9: 1218598; 10: 1273462 | 5120395 | 1280098.75
Total Unit #11 SS (Not Plant) | [13 empty] | 0 | 0
Total Unit #10 SS (Not Plant) | [13 empty] | 0 | 0
[14 empty] | 0 | 0
TOTAL STATION POWER |  | 7: 1786153; 8: 1778088; 9: 1613890; 10: 1721624 | 6899755 | 1724938.75
KWH | [13 empty] | 0
ENERGY DISTRIBUTION | [13 empty] | 0
0
0
0
0
GROSS ENERGY DISTRIBUTION | [13 empty] | 0
Gross Electric Energy Produced |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
Gross Energy Used in Water Plants |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
PLANT TOTAL GROSS ENERGY USED |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
0
NET ENERGY DISTRIBUTION | [13 empty] | 0
Net Electricity to Distribution |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
Net Energy used on water to distribution |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
PLANT TOTAL NET ENERGY USED |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
0
Plant Service / Gross Output |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
0
BTU's | [13 empty] | 0
Fuel No. 2 Consumed (BTU's) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
Fuel No. 6 Consumed (BTU's) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
TOTAL ENERGY IN FUEL |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
0
GROSS ENERGY DISTRIBUTION | [13 empty] | 0
Gross Electric Energy Produced |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
Gross Energy Used in Water Plants |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
PLANT TOTAL GROSS ENERGY USED |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
0
NET ENERGY DISTRIBUTION | [13 empty] | 0
Net Electricity to Distribution |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
Net Energy used on water to distribution |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
PLANT TOTAL NET ENERGY USED |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
0
Plant Service / NET Output |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
0
EFFICIENCY | [13 empty] | 0
0
Gross Efficiency | [13 empty] | 0
Electric Generating Plant Only |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
Water Desalination Plant only |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
Combined Generating and Water Plant |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
0
Net Efficiency | [13 empty] | 0
Electric Generating Plant Only |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
Water Desalination Plant only |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
Combined Generating and Water Plant |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
0
Heat Rates BTU/KWH | [13 empty] | 0
0
Gross Heat Rate | [13 empty] | 0
Electric Generating Plant Only |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
Water Desalination Plant only |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
Combined Generating and Water Plant |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
0
Net Heat Rate | [13 empty] | 0
Electric Generating Plant Only |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
Water Desalination Plant only |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
Combined Generating and Water Plant |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
[14 empty] | 0 | 0
pag4 | [13 empty] | 0 | 0
Desalination Plants Summary | [13 empty] | 0 | 0
Unit Service HRS | [13 empty] | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit Output GALS | [13 empty] | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
From TC |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
RO WAPA Meter |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
RO 7Seas water Meter 1 |  | 7: 37516000; 8: 39683000; 9: 32676000; 10: 37374000 | 147249000 | 36812250
RO 7Seas water Meter 2 |  | 7: 37390000; 8: 39542000; 9: 32563000; 10: 37249000 | 146744000 | 36686000
RO Meter Average |  | 7: 37453000; 8: 39612500; 9: 32619500; 10: 37311500 | 146996500 | 36749125
RO 7Seas ANNEXwater Meter 1 |  | 7: 53489000; 8: 49507000; 9: 50040000; 10: 50630000
RO 7Seas ANNEX water Meter 2 |  | 7: 53630000; 8: 49527000; 9: 50154000; 10: 50942000
RO 7Seas ANNEX water Meter 3 |  | 7: 53484000; 8: 49494000; 9: 50066000; 10: 50643000
RO Meter Average |  | 7: 53534333.3333; 8: 49509333.3333; 9: 50086666.6667; 10: 50738333.3333 | 203868666.6667 | 50967166.6667
STX TOTALS |  | 7: 90987333.3333; 8: 89121833.3333; 9: 82706166.6667; 10: 88049833.3333 | 350865166.6667 | 87716291.6667
Unit Cond LBS | [13 empty] | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
STX TOTALS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit LP Steam LBS | [13 empty] | 0 | 0
[14 empty] | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
STX TOTALS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit HP Steam LBS | [13 empty] | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
STT TOTALS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit Utilization Factor Percent | [13 empty] | 0% | 0%
IDE 3 | [13 empty] | 0% | 0% | bar: 7 to 10
IDE 4 | [13 empty] | 0% | 0% | bar: 7 to 10
IDE 5 | [13 empty] | 0% | 0% | bar: 7 to 10
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0% | 0%
Boilers Summary | [13 empty] | 0 | 0
Service Hrs | [13 empty] | 0 | 0
WHB 21 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
HRSG 24 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Boiler 11 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
This Month Gals | [13 empty] | 0 | 0
WHB 21 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
HRSG 24 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Boiler 11 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
TOTALS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
This Month LP STM LBS | [13 empty] | 0 | 0
WHB 21 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
HRSG 24 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Boiler 11 | [13 empty] | 0 | 0
TOTALS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
This Month HP STM LBS | [13 empty] | 0 | 0
WHB 21 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
HRSG 24 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
|  | 0 | 0 | 0 | 0
Boiler 11 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
TOTALS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Water Distribution | [13 empty] | 0 | 0
Total Water Produced |  | 7: 90987333.3333; 8: 89121833.3333; 9: 82706166.6667; 10: 88049833.3333 | 350865166.6667 | 87716291.6667
Total to Distribution Tank |  | 7: 89206406.6667; 8: 87271346.6667; 9: 81464380; 10: 86830084.6667 | 344772218 | 86193054.5
Apparent Station Use |  | 7: 1780926.6667; 8: 1850486.6667; 9: 1241786.6667; 10: 1219748.6667 | 6092948.6667 | 1523237.1667
Water to day Tank (Booster) Plus UPW Product |  | 7: 1151333.3333; 8: 1244333.3333; 9: 1259000; 10: 1001333.3333 | 4656000 | 1164000
Water to the Demineralizer(regen) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Boilers Make Up |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 16 Noxwater |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 17 Noxwater |  | 7: 8237911.2549; 8: 813283.4473; 9: 756803.4668; 10: 825476.5625 | 10633474.7314 | 2658368.6829
Unit 19 Noxwater |  | 7: 136276.123; 8: 214627.1973; 9: 360488.5254; 10: 39235.8398 | 750627.6855 | 187656.9214
Unit 20 Noxwater |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Total Wtr to NOX |  | 7: 1007500; 8: 1094100; 9: 1093700; 10: 849900 | 4045200 | 1011300
Station Wtr Warehouse & Eng. |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Plant Service Water |  | 7: 26900; 8: 17300; 9: 20400; 10: 50600 | 115200 | 28800
Admin. Off. Water |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
WTR to Fire Hydrants |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Total Water Used |  | 7: 1780926.6667; 8: 1850486.6667; 9: 1241786.6667; 10: 1219748.6667 | 6092948.6667 | 1523237.1667
Unaccountable Water |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Steam Summary | [13 empty] | 0 | 0
LP Steam LBS | [13 empty] | 0 | 0
Total Steam Produced |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
From Steam Turbine 10 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
From Steam Turbine 11 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
[14 empty] | 0 | 0
HP STM to IDE's Ejectors | [13 empty] | 0 | 0
LP STM to IDE's Process |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Used Steam for Production |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
[14 empty] | 0 | 0
Others uses & Deareator |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
HP Steam LBS | [13 empty] | 0 | 0
Total Steam Produced |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
To Steam Turbine 10 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
To Steam Turbine 11 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
From Steam Turbines |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
HP STM to IDE's Ejectors |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
LP STM to IDE's Process | [13 empty] | 0 | 0
Used Steam for Production |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
[14 empty] | 0 | 0
Others uses & Deareator |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Boiler MUF from MUF Meters |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Boiler MUF from Desal Unit HPSTM Meters |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Boilers MUF per Desal Design Quantities |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
LPSTM to Desal/Condensate Return | [13 empty] | 0% | 0% | bar: 7 to 10
Boiler 10 MUF/HPSTM Generated | [13 empty] | 0% | 0%
Boiler 11 MUF/HPSTM Generated |  | 7: N/A; 8: N/A; 9: N/A; 10: N/A | 0% | 0%
WHB MUF / HP & LPSTM Generated |  | 7: N/A; 8: N/A; 9: N/A; 10: N/A | 0 | 0
[14 empty] | 0% | 0%
pag5 | [13 empty] | 0% | 0%
Feeder KWH | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 7: 1360494.62; 8: 1358974.88; 9: 1203228; 10: 1236634 | 5159331.5 | 1289832.875
Feeder # 2 (13 Kv) |  | 7: 3241831.56; 8: 3157129.75; 9: 2883075; 10: 2859160.25 | 12141196.56 | 3035299.14
Feeder # 3 (13(Kv) |  | 7: 1111674; 8: 1126770; 9: 1084143; 10: 1086359 | 4408946 | 1102236.5
Feeder # 4 (13 Kv) |  | 7: 1542316.75; 8: 1558387; 9: 1484825; 10: 1499464.5 | 6084993.25 | 1521248.3125
Feeder # 5 (13 Kv) |  | 7: 3890000; 8: 3720000; 9: 3630000; 10: 3620000 | 14860000 | 3715000
Feeder # 6 (13 Kv) |  | 7: 2272777; 8: 2244390; 9: 2070676; 10: 2085241 | 8673084 | 2168271
Feeder # 9A (13 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 6B (24 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 8 (24 Kv) |  | 7: 4999139.5; 8: 5863816.5; 9: 6954336; 10: 7030357 | 24847649 | 6211912.25
Feeder # 9B (24Kv) |  | 7: 4274225.25; 8: 2607787.671; 9: 0; 10: 0 | 6882012.921 | 3441006.4605
Feeder # 10A (24 Kv) |  | 7: 0; 8: 832165; 9: 1843955; 10: 1859330 | 4535450 | 1511816.6667
Feeder # 10 (24 Kv) |  | 7: 1532181; 8: 1548799.5; 9: 1485914.75; 10: 1507122.75 | 6074018 | 1518504.5
TOTALS |  | 7: 24224639.68; 8: 24018220.301; 9: 22640152.75; 10: 22783668.5 | 93666681.231 | 23416670.3078
Feeder Planned Outages | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 2 (13 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 3 (13(Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 4 (13 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 5 (13 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 6 (13 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 6B (24 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0
Feeder # 8 (24 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 9 (24Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 10 (24 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
TOTALS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder Forced Outages | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 7: 1; 8: 2; 9: 4; 10: 1 | 8 | 2
Feeder # 2 (13 Kv) |  | 7: 9; 8: 2; 9: 7; 10: 4 | 22 | 5.5
Feeder # 3 (13(Kv) |  | 7: 1; 8: 3; 9: 5; 10: 3 | 12 | 3
Feeder # 4 (13 Kv) |  | 7: 1; 8: 3; 9: 5; 10: 2 | 11 | 2.75
Feeder # 5 (13 Kv) |  | 7: 1; 8: 2; 9: 2; 10: 1 | 6 | 1.5
Feeder # 6 (13 Kv) |  | 7: 1; 8: 1; 9: 5; 10: 1 | 8 | 2
Feeder # 6B (24 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0
Feeder # 8 (24 Kv) |  | 7: 4; 8: 1; 9: 1; 10: 1 | 7 | 1.75
Feeder # 9 (24Kv) |  | 7: 2; 8: 1; 9: 0; 10: 0 | 3 | 1.5
Feeder # 10 (24 Kv) |  | 7: 0; 8: 4; 9: 11; 10: 2 | 17 | 5.6667
TOTALS |  | 7: 20; 8: 19; 9: 40; 10: 15 | 94 | 23.5
Feeder Total Outages HRS | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 7: 0.41667; 8: 2.25; 9: 1.5833; 10: 1.9 | 6.15 | 1.5375
Feeder # 2 (13 Kv) |  | 7: 1.75; 8: 15.9167; 9: 3.45; 10: 2.9833 | 24.1 | 6.025
Feeder # 3 (13(Kv) |  | 7: 0.43333; 8: 4.35; 9: 2.85; 10: 0.53333 | 8.1667 | 2.0417
Feeder # 4 (13 Kv) |  | 7: 0.81667; 8: 3.0167; 9: 3.1833; 10: 2.3333 | 9.35 | 2.3375
Feeder # 5 (13 Kv) |  | 7: 0.41667; 8: 2.2333; 9: 0.81667; 10: 0.033333 | 3.5 | 0.875
Feeder # 6 (13 Kv) |  | 7: 0.83333; 8: 2.8167; 9: 3.05; 10: 1.9 | 8.6 | 2.15
Feeder # 6B (24 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0
Feeder # 8 (24 Kv) |  | 7: 1.3833; 8: 2.2833; 9: 0.73333; 10: 0.033333 | 4.4333 | 1.1083
Feeder # 9 (24Kv) |  | 7: 2.1; 8: 2.8333; 9: 0; 10: 0 | 4.9333 | 2.4667
Feeder # 10 (24 Kv) |  | 7: 0; 8: 6.5667; 9: 3.9167; 10: 2.1833 | 12.6667 | 4.2222
Feeder loss sales KWH | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 7: 762.3527; 8: 4122.2696; 9: 2651.819; 10: 3166.1563 | 10702.5977 | 2675.6494
Feeder # 2 (13 Kv) |  | 7: 7643.2539; 8: 69018.1735; 9: 13881.2487; 10: 11510.9801 | 102053.6562 | 25513.4141
Feeder # 3 (13(Kv) |  | 7: 647.8577; 8: 6626.7147; 9: 4308.4537; 10: 779.3106 | 12362.3367 | 3090.5842
Feeder # 4 (13 Kv) |  | 7: 1694.8156; 8: 6344.4532; 9: 6594.0053; 10: 4717.4164 | 19350.6905 | 4837.6726
Feeder # 5 (13 Kv) |  | 7: 2179.7602; 8: 11200.2876; 9: 4122.0366; 10: 162.1936 | 17664.278 | 4416.0695
Feeder # 6 (13 Kv) |  | 7: 2548.5277; 8: 8529.1968; 9: 8808.9292; 10: 5338.8464 | 25225.5001 | 6306.375
Feeder # 6B (24 Kv) |  | 7: 0; 8: 0; 9: 0; 10: 0
Feeder # 8 (24 Kv) |  | 7: 9312.3096; 8: 18051.4316; 9: 7090.3416; 10: 314.9943 | 34769.0771 | 8692.2693
Feeder # 9 (24Kv) |  | 7: 12098.4944; 8: 9969.0556; 9: 0; 10: 0 | 22067.5501 | 11033.775
Feeder # 10 (24 Kv) |  | 7: 0; 8: 13791.6875; 9: 8127.3121; 10: 4435.8013 | 26354.8009 | 8784.9336
TOTALS |  | 7: 36887.3718; 8: 147653.2701; 9: 55584.1463; 10: 30425.699 | 270550.4872 | 67637.6218
Plant Feeder Total Planned Outages | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 2 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 3 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 4 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 5 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 6 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 9 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 10 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
TOTALS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Plant Feeder Total Forced Outages | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 0; 8: 2; 9: 4; 10: 0 | 6 | 3
Feeder # 2 |  | 7: 9; 8: 2; 9: 7; 10: 4 | 22 | 5.5
Feeder # 3 |  | 7: 0; 8: 3; 9: 5; 10: 3 | 11 | 3.6667
Feeder # 4 |  | 7: 0; 8: 3; 9: 5; 10: 2 | 10 | 3.3333
Feeder # 5 |  | 7: 0; 8: 2; 9: 2; 10: 0 | 4 | 2
Feeder # 6 |  | 7: 0; 8: 0; 9: 5; 10: 0 | 5 | 5
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 4; 8: 0; 9: 0; 10: 0 | 4 | 4
Feeder # 9 |  | 7: 2; 8: 0; 9: 0; 10: 0 | 2 | 2
Feeder # 10 |  | 7: 0; 8: 4; 9: 11; 10: 2 | 17 | 5.6667
TOTALS |  | 7: 15; 8: 16; 9: 39; 10: 11 | 81 | 20.25
Plant Feeder Total Outages Time | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 0.41667; 8: 2.25; 9: 1.5833; 10: 1.9 | 6.15 | 1.5375
Feeder # 2 |  | 7: 1.75; 8: 15.9167; 9: 3.45; 10: 2.9833 | 24.1 | 6.025
Feeder # 3 |  | 7: 0.43333; 8: 4.35; 9: 2.85; 10: 0.53333 | 8.1667 | 2.0417
Feeder # 4 |  | 7: 0.81667; 8: 3.0167; 9: 3.1833; 10: 2.3333 | 9.35 | 2.3375
Feeder # 5 |  | 7: 0.41667; 8: 2.2333; 9: 0.81667; 10: 0.033333 | 3.5 | 0.875
Feeder # 6 |  | 7: 0.83333; 8: 2.8167; 9: 3.05; 10: 1.9 | 8.6 | 2.15
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 1.3833; 8: 2.2833; 9: 0.73333; 10: 0.033333 | 4.4333 | 1.1083
Feeder # 9 |  | 7: 2.1; 8: 2.8333; 9: 0; 10: 0 | 4.9333 | 2.4667
Feeder # 10 |  | 7: 0; 8: 6.5667; 9: 3.9167; 10: 2.1833 | 12.6667 | 4.2222
TOTALS | [13 empty] | 0 | 0
Plant Feeder Total Loss sales | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 762.3527; 8: 4122.2696; 9: 2651.819; 10: 3166.1563 | 10702.5977 | 2675.6494
Feeder # 2 |  | 7: 7643.2539; 8: 69018.1735; 9: 13881.2487; 10: 11510.9801 | 102053.6562 | 25513.4141
Feeder # 3 |  | 7: 647.8577; 8: 6626.7147; 9: 4308.4537; 10: 779.3106 | 12362.3367 | 3090.5842
Feeder # 4 |  | 7: 1694.8156; 8: 6344.4532; 9: 6594.0053; 10: 4717.4164 | 19350.6905 | 4837.6726
Feeder # 5 |  | 7: 2179.7602; 8: 11200.2876; 9: 4122.0366; 10: 162.1936 | 17664.278 | 4416.0695
Feeder # 6 |  | 7: 2548.5277; 8: 8529.1968; 9: 8808.9292; 10: 5338.8464 | 25225.5001 | 6306.375
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 9312.3096; 8: 18051.4316; 9: 7090.3416; 10: 314.9943 | 34769.0771 | 8692.2693
Feeder # 9 |  | 7: 12098.4944; 8: 9969.0556; 9: 0; 10: 0 | 22067.5501 | 11033.775
Feeder # 10 |  | 7: 0; 8: 13791.6875; 9: 8127.3121; 10: 4435.8013 | 26354.8009 | 8784.9336
TOTALS |  | 7: 36887.3718; 8: 147653.2701; 9: 55584.1463; 10: 30425.699 | 270550.4872 | 67637.6218
Line Feeder Total Planned Outages | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 2 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 3 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 4 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 5 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 6 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 9 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 10 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
TOTALS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Line Feeder Total Forced Outages | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 1; 8: 0; 9: 0; 10: 1 | 2 | 1
Feeder # 2 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 3 |  | 7: 1; 8: 0; 9: 0; 10: 0 | 1 | 1
Feeder # 4 |  | 7: 1; 8: 0; 9: 0; 10: 0 | 1 | 1
Feeder # 5 |  | 7: 1; 8: 0; 9: 0; 10: 1 | 2 | 1
Feeder # 6 |  | 7: 1; 8: 1; 9: 0; 10: 1 | 3 | 1
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 0; 8: 1; 9: 1; 10: 1 | 3 | 1
Feeder # 9 |  | 7: 0; 8: 1; 9: 0; 10: 0 | 1 | 1
Feeder # 10 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
TOTALS |  | 7: 5; 8: 3; 9: 1; 10: 4 | 13 | 3.25
Line Feeder Total Outages Time | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 2 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 3 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 4 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 5 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 6 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 9 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 10 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
TOTALS | [13 empty] | 0 | 0
Line Feeder Total Loss sales | [13 empty] | 0 | 0
Feeder # 1 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 2 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 3 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 4 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 5 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 6 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 6B (24 Kv)
Feeder # 8 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 9 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Feeder # 10 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
TOTALS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
pag6 | [13 empty] | 0 | 0
Units Outages | [13 empty] | 0 | 0
Unit 10 ST | [13 empty] | 4 | 1 | bar: 7 to 10
Unit 11 ST | [13 empty] | 4 | 1 | bar: 7 to 10
Unit 11 BLR | [13 empty] | 4 | 1 | bar: 7 to 10
Unit 16 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 17 |  | 7: 1; 8: 1; 9: 2; 10: 0 | 4 | 1.3333
Unit 19 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 20 | [13 empty] | 4 | 1 | bar: 7 to 10
Aggreko |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
HRSG 21 | [13 empty] | 4 | 1 | bar: 7 to 10
HRSG 24 |  | 7: 0; 8: 0; 9: 0; 10: 0
Units Outages Duration | [13 empty] | 0 | 0
Unit 10 ST |  | 7: 744; 8: 744; 9: 720; 10: 744 | 2952 | 738
Unit 11 ST |  | 7: 744; 8: 744; 9: 720; 10: 744 | 2952 | 738
Unit 11 BLR |  | 7: 744; 8: 744; 9: 720; 10: 744 | 2952 | 738
Unit 16 |  | 7: 744; 8: 744; 9: 720; 10: 744 | 2952 | 738
Unit 17 |  | 7: 0; 8: 0; 9: 26.65; 10: 0 | 26.65 | 26.65
Unit 19 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 20 |  | 7: 744; 8: 744; 9: 720; 10: 744 | 2952 | 738
Aggreko |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
HRSG 21 |  | 7: 744; 8: 744; 9: 720; 10: 744 | 2952 | 738
HRSG 24 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit Planned Outages | [13 empty] | 0 | 0
Unit 10 ST | [13 empty] | 4 | 1 | bar: 7 to 10
Unit 11 ST | [13 empty] | 4 | 1 | bar: 7 to 10
Unit 11 BLR | [13 empty] | 4 | 1 | bar: 7 to 10
Unit 16 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 17 |  | 7: 1; 8: 1; 9: 0; 10: 0 | 2 | 1
Unit 19 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 20 | [13 empty] | 4 | 1 | bar: 7 to 10
Aggreko |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
HRSG 21 | [13 empty] | 4 | 1 | bar: 7 to 10
HRSG 24 |  | 7: 0; 8: 0; 9: 0; 10: 0
Unit Planned Outages Duration | [13 empty] | 0 | 0
Unit 10 ST |  | 7: 744; 8: 744; 9: 720; 10: 744 | 2952 | 738
Unit 11 ST |  | 7: 744; 8: 744; 9: 720; 10: 744 | 2952 | 738
Unit 11 BLR |  | 7: 744; 8: 744; 9: 720; 10: 744 | 2952 | 738
Unit 16 |  | 7: 744; 8: 744; 9: 720; 10: 744 | 2952 | 738
Unit 17 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 19 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 20 |  | 7: 744; 8: 744; 9: 720; 10: 744 | 2952 | 738
Aggreko |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
HRSG 21 |  | 7: 744; 8: 744; 9: 720; 10: 744 | 2952 | 738
HRSG 24 |  | 7: 0; 8: 0; 9: 0; 10: 0
Unit Forced Outages |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 10 ST |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 11 ST |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 11 BLR |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 16 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 17 |  | 7: 0; 8: 0; 9: 2; 10: 0 | 2 | 2
Unit 19 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 20 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Aggreko |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
HRSG 21 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
HRSG 24 |  | 7: 0; 8: 0; 9: 0; 10: 0
Unit Forced Outages Duration |  | 7: 0; 8: 0; 9: 2; 10: 0 | 2 | 2
Unit 10 ST |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 11 ST |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 11 BLR |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 16 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 17 |  | 7: 0; 8: 0; 9: 26.65; 10: 0 | 26.65 | 26.65
Unit 19 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 20 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Aggreko |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 3 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 4 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 5 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
IDE 9 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
HRSG 21 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
HRSG 24 |  | 7: 0; 8: 0; 9: 0; 10: 0
Plant Power Distribution | [13 empty] | 0 | 0
Total 13KV Feeders |  | 7: 13419093.93; 8: 13165651.63; 9: 12355947; 10: 12386858.75 | 51327551.31 | 12831887.8275
Total 24KV Feeders |  | 7: 10805545.75; 8: 10852568.671; 9: 10284205.75; 10: 10396809.75 | 42339129.921 | 10584782.4803
Feeder Totals |  | 7: 24224639.68; 8: 24018220.301; 9: 22640152.75; 10: 22783668.5 | 93666681.231 | 23416670.3078
Total Generation |  | 7: 25719989.5; 8: 25797063.5; 9: 24243512.5; 10: 24404586 | 100165151.5 | 25041287.875
24 KV BUS at XFMR-1 (T1) |  | 7: 66909.75; 8: 391221.84; 9: 1276007.57; 10: 55735.12 | 1789874.28 | 447468.57
24 KV BUS at XFMR-2 (T2) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
24 KV BUS at XFMR-3 (T3) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
XFMR T1 in |  | 7: 66510; 8: 389244; 9: 1270567; 10: 55447
XFMR T1 out |  | 7: 4351087; 8: 4122766; 9: 4142281; 10: 5145701
XFMR T3 in |  | 7: 0; 8: 0; 9: 0; 10: 0
XFMR T3 out |  | 7: 0; 8: 0; 9: 0; 10: 0
XFMR T4in (from #16) |  | 7: 0; 8: 0; 9: 0; 10: 0
XFMR T4 out ( |  | 7: 0; 8: 0; 9: 0; 10: 0
XFMR T5 in (from #20) |  | 7: 0; 8: 99999416; 9: 584; 10: 0
XFMR T5 out |  | 7: 5558411; 8: 5172388; 9: 4438906; 10: 4536047
T1 &T3&T4 & T5 Available |  | 7: 9976008; 8: 109683814; 9: 9852338; 10: 9737195 | 139249355 | 34812338.75
T1 &T3 & T4 & T5 Losses |  | 7: 47669.07; 8: 366338.699; 9: 251331.5; 10: 237737.5 | 903076.769 | 225769.1922
Net Distributed |  | 7: 25672320.43; 8: 25430724.801; 9: 23992181; 10: 24166848.5 | 99262074.731 | 24815518.6828
Line Department |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Water Department |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Power Plant Services |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Administration & General |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Plant Station Service |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Net Available from Bus |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Wapa KWH From Dist |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
SwitchGear Bkr1 SS |  | 7: 1126712.5; 8: 1097708.5; 9: 1046123; 10: 1076282.5 | 4346826.5 | 1086706.625
SwitchGear Bkr3 SS |  | 7: 301288.25; 8: 306636; 9: 302425.25; 10: 302817.5 | 1213167 | 303291.75
Total Station Service Power |  | 7: 1437840.75; 8: 1408424.5; 9: 1350288.25; 10: 1381140 | 5577693.5 | 1394423.375
Net KWH Available for Sale |  | 7: 24234479.68; 8: 24022300.301; 9: 22641892.75; 10: 22785708.5 | 93684381.231 | 23421095.3078
Plant Unaccountable |  | 7: 0; 8: 0; 9: 0; 10: 0
Peak Load: |  | 7: 41080; 8: 41790; 9: 40070; 10: 39340 | 162280 | 40570
Day |  | 7: Thursday; 8: Sunday; 9: Tuesday; 10: Saturday |  | 0
Date |  | 7: 2020-07-02; 8: 2020-08-16; 9: 2020-09-29; 10: 2020-10-10
Hour |  | 7: 19:20; 8: 19:21; 9: 19:00; 10: 18:39
Min Load |  | 7: 27650; 8: 26320; 9: 25710; 10: 25910 | 105590 | 26397.5
Day |  | 7: Sunday; 8: Wednesday; 9: Sunday; 10: Thursday
Date |  | 7: 2020-07-19; 8: 2020-08-05; 9: 2020-09-20; 10: 2020-10-29
Hour |  | 7: 6:00; 8: 6:00; 9: 4:00; 10: 3:00 |  | 4:45
Pag 7
No 6 Fuel For Power |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
No 6 Fuel For Water |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
No 2 Fuel For Power |  | 7: 5520.1249; 8: 9234.3241; 9: 16758.6572; 10: 1935.0103 | 33448.1166 | 8362.0292
No 2 Fuel For Water |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
O&M Factor for Water |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
BLR11FUEL2COST |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Firing | [13 empty] | 0 | 0
WHBSFCAE |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Power Boilers | [13 empty] | 0 | 0
[14 empty] | 0 | 0
TPBSFC | [13 empty] | 0 | 0
BLR11FUELCOST |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Combined Cycle | [13 empty] | 0 | 0
WHB, 16 & 17 | [13 empty] | 0 | 0
TGTFC | [13 empty] | 0 | 0
GEN161720FUELCOST |  | 7: 1999545.5291; 8: 1924719.682; 9: 1614411.4254; 10: 1804814.6582 | 7343491.2947 | 1835872.8237
Simple Cycle | [13 empty] | 0 | 0
12 & 14 & 22 | [13 empty] | 0 | 0
GEN 19FUELCOST |  | 7: 343756.9591; 8: 495210.025; 9: 787472.5538; 10: 88884.4036 | 1715323.9414 | 428830.9854
DIESEL | [13 empty] | 0 | 0
7 St. John | [13 empty] | 0 | 0
DIESEL_EMER. |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
GT Fuel Allocation | [13 empty] | 0 | 0
HP Stm from WHB | [13 empty] | 0 | 0
GTFCAE | [13 empty] | 0 | 0
WHBHPSTMCOST |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
whb Benefit | [13 empty] | 0 | 0
Equalization to Water | [13 empty] | 0 | 0
WHBBECW | [13 empty] | 0 | 0
WHBBENCOSTWTR |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Extraction Benefit | [13 empty] | 0 | 0
Equalization to Water | [13 empty] | 0 | 0
BECW | [13 empty] | 0 | 0
BENEQFCOSTWTR |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Gas Turbine | [13 empty] | 0 | 0
Power Allocation | [13 empty] | 0 | 0
GTFCA | [13 empty] | 0 | 0
GEN161720ADJFCOST |  | 7: 1999545.5291; 8: 1924719.682; 9: 1614411.4254; 10: 1804814.6582 | 7343491.2947 | 1835872.8237
Extraction Incremental | [13 empty] | 0 | 0
to Water | [13 empty] | 0 | 0
FCAWI | [13 empty] | 0 | 0
INCRFUELCOSTWTR |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
GT Fuel Allocation | [13 empty] | 0 | 0
LP Stm from WHB | [13 empty] | 0 | 0
WHBFCAW | [13 empty] | 0 | 0
WHBLPSTMCOST |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Electrc Power | [13 empty] | 0 | 0
Generation | [13 empty] | 0 | 0
TOTFUELCOSTPWR |  | 7: 3713314.5045; 8: 3744752.5614; 9: 3562453.9143; 10: 3315497.8093 | 14336018.7894 | 3584004.6974
RO Electricity cost |  | 7: 70963.9268; 8: 74207.1698; 9: 62238.2739; 10: 65426.4231 | 272835.7935 | 68208.9484
UPW Electicity Cost |  | 7: 2771.5908; 8: 2670.0228; 9: 2442.0318; 10: 2235.9573 | 10119.6027 | 2529.9007
RO Annex Electricity cost |  | 7: 96033.7397; 8: 88297.0049; 9: 89701.1334; 10: 84224.1728
TOTFUELCSRWTR |  | 7: 166997.6665; 8: 162504.1747; 9: 151939.4073; 10: 149650.5959 | 631091.8443 | 157772.9611
Pag8 | [13 empty] | 0 | 0
No 2 BBLS | [13 empty] | 0 | 0
Inventory-Beginning of Month |  | 7: 39740.5629; 8: 34220.4379; 9: 57168.2338; 10: 40409.5766 | 171538.8112 | 42884.7028
Received During Month |  | 7: 0; 8: 32182.12; 9: 0; 10: 0 | 32182.12 | 32182.12
Consumed During Month |  | 7: 5520.1249; 8: 9234.3241; 9: 16758.6572; 10: 1935.0103 | 33448.1166 | 8362.0292
Inventory-End of Month |  | 7: 34220.4379; 8: 57168.2338; 9: 40409.5766; 10: 38474.5663 | 170272.8146 | 42568.2037
Calorific Value (BTU/GAL) |  | 7: 136784.2908; 8: 136999.0879; 9: 136999.0879; 10: 136999.0879 | 547781.5546 | 136945.3886
Calorific Value (BTU/GAL) |  | 7: 136784.2908; 8: 136999.0879; 9: 136999.0879; 10: 136999.0879 | 547781.5546 | 136945.3886
No 6 BBLS | [13 empty] | 0 | 0
Inventory-Beginning of Month |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Received During Month |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Consumed During Month |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Inventory-End of Month |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Calorific Value (BTU/GAL) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
PROPANE
Propane Value (BTU/Gal) |  | 7: 91735; 8: 91735; 9: 91735; 10: 91647
End of Month- Fuel in Tanks | [13 empty] | 0 | 0
No 2 BBLS | [13 empty] | 0 | 0
Tank 1 #2 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Tank 2 #2 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Tank 5 #2 |  | 7: 8440.91; 8: 37021.4; 9: 30852.38; 10: 28860.59 | 105175.28 | 26293.82
Tank 6 #2 |  | 7: 17422.64; 8: 11760.45; 9: 1141.19; 10: 1124.68 | 31448.96 | 7862.24
TOTAL |  | 7: 34220.44; 8: 57168.23; 9: 40409.58; 10: 38474.57 | 170272.82 | 42568.205
No 6 BBLS | [13 empty] | 0 | 0
Tank 3 #2 |  | 7: 4452.57; 8: 4450.29; 9: 4453.2; 10: 4451.44 | 17807.5 | 4451.875
Tank 4 #6 |  | 7: 3904.33; 8: 3936.1; 9: 3962.8; 10: 4037.85 | 15841.08 | 3960.27
Tank 7 #6 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
TOTAL |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
Fuel Shipments | [13 empty] | 0 | 0
Date(1) |  | 7: 0; 8: 2020-08-19; 9: 0; 10: 0 | 2020-08-19 | 2020-08-19
No2 BBLS |  | 7: 0; 8: 32182.12; 9: 0; 10: 0 | 32182.12 | 32182.12
Date(2) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Date(3) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Date(4) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Date(5) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Date(6) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Date(7) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Date(8) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Date(9) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
No2 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
TOTAL SHIPMENTS No 2 |  | 7: 0; 8: 32182.12; 9: 0; 10: 0 | 32182.12 | 32182.12
Date(1) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Date(2) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Date(3) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Date(4) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Date(5) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Date(6) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Date(7) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Date(8) |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
No6 BBLS |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
TOTAL SHIPMENTS No 6 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
[14 empty] | 0 | 0
Fuel Allocations Amount | [13 empty] | 0 | 0
Electric Power Generation |  | 7: 3713314.5045; 8: 3744752.5614; 9: 3562453.9143; 10: 3315497.8093 | 14336018.7894 | 3584004.6974
Water Production |  | 7: 166997.6665; 8: 162504.1747; 9: 151939.4073; 10: 149650.5959 | 631091.8443 | 157772.9611
Total #2 Fuel Cost |  | 7: 426605.2954; 8: 639765.748; 9: 1161061.1421; 10: 134059.983 | 2361492.1684 | 590373.0421
BBLS No. 6 for Power |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
BBLS No.6 for Water |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
BBLS No. 2 for Power |  | 7: 5520.1249; 8: 9234.3241; 9: 16758.6572; 10: 1935.0103 | 33448.1166 | 8362.0292
BBLS No.2 for Water |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
No. 6 BBL Cost |  | 7: 71.9034; 8: 71.9034; 9: 71.9034; 10: 71.9034 | 287.6136 | 71.9034
No. 2 BBL Cost |  | 7: 77.2818; 8: 69.2813; 9: 69.2813; 10: 69.2813 | 285.1256 | 71.2814
Propane Cost per Bbl |  | 7: 38.3544; 8: 38.262; 9: 37.5354; 10: 38.1612
Propane Consumed
Unit 16 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0
Unit 17 |  | 7: 2098879.9746; 8: 1954076.7936; 9: 1388410.9176; 10: 1936648.7771 | 7378016.4629
Unit 20 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Aggreko |  | 7: 1683103.0254; 8: 1632631.2064; 9: 1468624.0824; 10: 1729528.2229 | 6513886.5371
No. 2 Units BBLS No. 2 Consumed | [13 empty] | 0 | 0
Unit 10 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 11 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 16 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Unit 17 |  | 7: 1072.0288; 8: 2086.5049; 9: 5392.3457; 10: 652.0604 | 9202.9399 | 2300.735
Unit 19 |  | 7: 4448.0961; 8: 7147.8192; 9: 11366.3115; 10: 1282.9499 | 24245.1767 | 6061.2942
Unit 20 |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Diesel Emergency |  | 7: 0; 8: 0; 9: 0; 10: 0 | 0 | 0
Total No. 2 Consumed |  | 7: 5520.1249; 8: 9234.3241; 9: 16758.6572; 10: 1935.0103 | 33448.1166 | 8362.0292
Note on I673: Nicholson: negative

## PR-Pag1
October - 2020
Production Summary |  |  |  |  | Generating Units Heat Rate |  | FYTD | This Month
|  | FYTD | FYTD |  | (Gross Energy in KWH Produced) | This Month | AVG. | %
Item | This Month | AVG. | TOTAL | Units | Units | BTU/KWH | BTU/KWH | Efficiency
Total System Gross Generation** | 24404.586 | 25041.2879 | 100165.1515 | MWH
Gross Power Plant Generation | 23735.79 | 24383.7325 | 97534.93 | MWH
Gross Water Production | 88049.8333 | 87716.2917 | 350865.1667 | KGAL
System Load Factor | 81.1% | 81.44% |  | % | Unit 10-Steam (10 MW) + WHBs* | N/A | N/A | N/A
Total Propane Fuel Cost | 3331088.4222 | 3151404.6163 | 12605618.4653 | $ | Unit 11-Steam (19.1 MW) + WHBs | N/A | N/A | N/A
Total No. 2 Fuel Cost | 134059.983 | 590373.0421 | 2361492.1684 | $ | Unit 16-Gas Turbine (22.5 MW) | 0 | 0 | 0%
Power Fuel Cost (Internal) | 0.14599 | 0.15341 |  | $/KWH | Unit 17-Gas Turbine (21.9 MW) | 20433.93 | 19863.22 | 16.7%
Power Fuel Cost (to bus) | 0.15209 | 0.15975 |  | $/KWH | Unit 19-Gas Turbine (24.5 MW) | 22369.83 | 24632.73 | 15.25%
Water Fuel Cost (Internal) | 1.6996 | 1.7989 |  | $/KGAL | Unit 20_Gas Turbine (24.5 MW) | 0 | 0 | 0%
Water Fuel Cost (to Distribution) | 1.7235 | 1.8307 |  | $/KGAL | Aggreko (20.0 MW) | 10904.21 | 10938.28 | 31.29%
Total Power Fuel Cost | 3315497.8093 | 3584004.6974 | 14336018.7894 | $ | Total Electric Generation Only | 14624.67 | 15032.05 | 23.33%
Total Water Cost | 149650.5959 | 157772.9611 | 631091.8443 | $ | *Note:Total Electric Generation includes values of steam provided to STG #10 and #11 by HRSGs
Propane consumed | 87289.9286 | 82689.8988 | 330759.5952 | BBLS
No. 2 Fuel Consumed | 1935.0103 | 8362.0292 | 33448.1166 | BBLS
[5 empty] | Power Units Availability |  | FYTD
No. 2 Fuel Received | 0 | 32182.12 | 32182.12 | BBLS |  | This Month | AVG.
[5 empty] | Unit | Percent (%) | Percent (%)
EOM No. 2 Fuel On Hand* | 19.2373 | 21.2841 |  | DAYS
Plant Water Use ( Internal | 1555.6764 | 5242.7176 | 20970.8704 | $ | Unit 10 | 0% | 0%
Plant Power Use (Internal) | 251337.0171 | 264568.2745 | 1058273.0981 | $ | Unit 11 | 0% | 0%
7SEAS RO 1 Electricity Cost | 65426.4231 |  |  | $ | Unit 16 | 0% | 0%
7SEAS UPW Electricity Cost | 2235.9573 |  |  | $ | Unit 17 | 100% | 99.07%
7SEAS RO 2 Electricity Cost | 84224.1728 |  |  | $ | Unit 19 | 100% | 100%
**Note: Includes power generated by solar |  |  |  |  | Unit 20 | 0% | 0%
*Note: Based on 2000Bbl/day consumption |  |  |  |  | Aggreko | 100% | 100%
[5 empty] | HRSG 21 | 0% | 0%
[5 empty] | HRSG 24 | 100% | 100%

## PR-Pag2
October - 2020
Power Generation - Station Power |  | FYTD | TOTAL | Generating Units Average Loading |  |  | FYTD | Utilization
Item | This Month | Monthly | FYTD |  |  | This Month | AVG. | Factor
| KWH | AVG. | KWH | (KWH / Operating Hours) |  | KW | KW | Percent
Steam Turbine Generation | 0 | 0 | 0 | Unit 10 |  | 0 | 0 | 0%
Gas Turbine Generation | 23735790 | 24383732.5 | 97534930 | Unit 11 |  | 0 | 0 | 0%
Diesel Generation | 0 | 0 | 0 | Unit 16 |  | 0 | 0 | 0%
Total Generation | 23735790 | 24383732.5 | 97534930 | Unit 17 |  | 12180.1154 | 13121.1915 | 55.62%
Steam Station Power | 0 | 0 | 0 | Unit 19 |  | 7875.895 | 7701.1257 | 32.15%
Gas Turbine Station Power | 36910 | 44315 | 177260 | Unit 20 |  | 0 | 0 | 0%
Aggreko Station Service | 670 | 870 | 3480 | Aggreko |  | 19615 | 19563.75 | 98.08%
Total Gen. Plant Station Power | 36910 | 44315 | 177260 | Diesel |  | 0 | 0 | 0%
Total Service / Gross Output | 0.1555% | 0.1818%
IPP1 | 668796 | 657555.375 | 2630221.5
Total System Generation | 24404586 | 24383732.5 | 97534930
Generating Units Station Power
Generating Units Operating Hours |  | FYTD | TOTAL |  |  | FYTD | TOTAL | This Month | FYTD | FYTD
| This Month | Monthly | FYTD |  | This Month | AVG. | FYTD | SS Power | AVG. | SS Power
Unit | HRS | AVG. | HRS | Unit | KWH | KWH | KWH | KWH | KWH | KWH
Unit 10 | 0 | 0 | 0 | Unit 10 | 0 | 0 | 0 | 0 | 0 | 0
Unit 11 | 0 | 0 | 0 | Unit 11 | 0 | 0 | 0 | 0 | 0 | 0
Unit 16 | 0 | 0 | 0 | Unit 16 | 0 | 0 | 0 | 0 | 0 | 0
Unit 17 | 728.2 | 700.25 | 2801 | Unit 17 | 8869560 | 9191620 | 36766480 | 2820 | 3725 | 14900
Unit 19 | 41.9 | 188.075 | 752.3 | Unit 19 | 330000 | 1535000 | 6140000 | 27680 | 33740 | 134960
Unit 20 | 0 | 0 | 0 | Unit 20 | 0 | 0 | 0 | 6410 | 6850 | 27400
Aggreko | 741.0772 | 697.6836 | 2790.7345 | Aggreko | 14536230 | 13657112.5 | 54628450 | 670 | 870 | 3480
Diesel Generation(Emergency) | 3 | 2.3333 | 7 | Diesel | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | TOTAL | 23735790 | 24383732.5 | 97534930 | 36910 | 44315 | 177260

## PR-Pag3
October - 2020
BOILERS/STM. TURBINES | SS | GAS TURBINE | SS | STX. EMERGENCY DIESEL | SS | OTHERS | SS
| Kwh |  | Kwh |  | Kwh |  | Kwh
SS10 Plant Aux. Trans 480V | 0 | Plant SS |  | Diesel | 0 | Station Service Shops | 27480
SS10 Unit Aux.. Trans 480V | 0 | Unit 16 | 0 |  |  | Station Service Office | 0
|  | Unit 17 | 780 |  |  | Fuel Tanks SS | 0
Unit 10 Total Station Power | 0 | Unit 19 | 27680 | TOTAL DIESEL | 0 | Switch Yard SS | 168000
|  | Unit 20 | 6410 |  |  | Richmond Sub SS
|  | Aggreko | 670 |  |  | Midland Sub SS
SS11 Plant Aux. Trans 480V | 0 |  |  |  |  | TOTAL OTHERS | 195480
SS11 Unit Aux.. Trans 480V | 0 | Unit SS |  | WATER PLANTS | SS
|  | Unit 16 | 0 |  | Kwh | SwitchGear Bkr1 SS | 1076282.5
Unit 11 Net Total Station Power | 0 | Unit 17 | 2040 | Plant ABC Pump usage | 0 | SwitchGear Bkr3 SS | 302817.5
|  | Unit 19 | 0 |  |  | SS10 Unit Aux Trans. | 0
|  | Unit 20 | 0 | Intake Pump A&B+Chloropac | 0 | SS11 Unit Aux Trans. | 0
HRSG 21 Station Power | 0 | TOTAL GAS TURBINES | 37580 |  |  | Total GT Unit SS | 2040
HRSG 24 Station Power** | 0 | Plant Pumps |  | RO Plant Electrical Usage | 448162
|  | Intake Pump A | 0 | UPW Electrical Usage | 15316 |  | 1381140
|  | Intake Pump B | 0 | RO ANNEX Electrical Usage | 576924
WHB Net Station Power | 0 | Intake Pump C | 0
TOTAL BOILERS / STM TURBINES | 0 |  |  | TOTAL WATER PLANTS | 1040402 | Total Station Service* | 1273462
*Total SS switched to a summaton of individual meters from general 'main' distribution meters summation
** No power to meter

## PR-Pag4
October - 2020
Desalination Plants Summary
|  | FYTD | TOTAL | Units Water Output
| Service | AVG. | FYTD | This Month | FYTD
Unit | HRS | HRS | HRS | GALS | GALS
RO 1 |  |  |  | 37311500 | 146996500
RO 2 |  |  |  | 50738333.3333 | 203868666.6667
STX TOTALS |  |  |  | 88049833.3333 | 350865166.6667
Boilers Summary
|  | Boilers Service Hours |  |  | Make Up Feed Water |  | Low Pressure Steam |  | High Pressure Steam
| Service | AVG. | FYTD | This Month | AVG. | FYTD | This Month | FYTD | This Month | FYTD
Unit | HRS | HRS | HRS | GALS | GALS | GALS | LBS | AVG. | LBS | AVG.
HRSG 21/IPOS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HRSG 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Boiler 11 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
TOTALS |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Distribution |  | This Month | FYTD-AVG. | FYTD |  | Steam Summary |  | LP Steam | HP Steam
|  | GALS | GALS | GALS |  | ITEM |  | LBS | LBS
Total Plant Water Produced |  | 88049833.3333 | 87716291.6667 | 350865166.6667 |  | Total Steam Produced |  | 0 | 0
Total Reverse Osmosis Produced |  | 88049833.3333 | 36749125 | 146996500 |  | To Steam Turbine 10 |  |  | 0
Total to Distribution Tank |  | 86830084.6667 | 86193054.5 | 344772218 |  | To Steam Turbine 11 |  |  | 0
Apparent Station Use |  | 1219748.6667 | 1523237.1667 | 6092948.6667 |  | From Steam Turbine 10 |  | 0 | 0
Water to day Tank |  | 1001333.3333 | 1164000 | 4656000 |  | From Steam Turbine 11 |  | 0
UPW Feed |  | 1169148.6667 | 1494437.1667 | 5977748.6667
UPW Product |  | 1001333.3333 | 1164000 | 4656000 |  | Used Steam for Production |  | 0 | 0
Water to the Demineralizer (Regen) |  | 0 | 0 | 0 |  | Others uses & Deareator |  |  | 0
Boilers Make Up |  | 0 | 0 | 0
Unit 16 Noxwater |  | 0 | 0 | 0
Unit 17 Noxwater |  | 825476.5625 | 2658368.6829 | 10633474.7314
Unit 19 Noxwater |  | 39235.8398 | 187656.9214 | 750627.6855
Unit 20 Noxwater |  | 0 | 0 | 0
Metered Total Wtr to NOX |  | 849900 | 1011300 | 4045200
Station Wtr Warehouse & Eng. |  | 0 | 0 | 0
Plant Service Water |  | 50600 | 28800 | 115200
Admin. Off. Water |  | 0 | 0 | 0
WTR to Fire Hydrants |  | 0 | 0 | 0 |  | * Unaccountable value has been zeroed due to non-functional distribution
Total Water used |  | 1219748.6667 | 1523237.1667 | 6092948.6667 |  |  | meter giving rise to high unaccountable value
Unaccountable Water |  | 0 | 0 | 0

## PR-Pag5
October - 2020
| Feeders Power Distribution |  | This Month Total Plant Outages |  |  | Month | FYTD | FYTD | Feeders Outages Summary
| Output | FYTD | Planned | Forced | Time Hrs | Lost Sales | Total | Total | Feeder | Time | Date | Reason
Feeder | KWH | AVG KWH | Outages | Outages | Duration | Kwh | Outages | Time Hrs |  | min.
[9 empty] | Feeder #10B | 29 | 2020-10-02 | Feeders tripped due to IPOS losing steam for their vaporizer
Feeder #1A (13Kv) | 1236634 | 1289832.875 | 0 | 1 | 1.9 | 3166.1563 | 6 | 6.15 | Feeder #2A | 30 | 2020-10-02 | Feeders tripped due to IPOS losing steam for their vaporizer
Feeder #2A (13 Kv) | 2859160.25 | 3035299.14 | 0 | 4 | 2.9833 | 11510.9801 | 22 | 24.1 | Feeder #3A | 24 | 2020-10-02 | Feeders tripped due to IPOS losing steam for their vaporizer
Feeder #3A (13(Kv) | 1086359 | 1102236.5 | 0 | 3 | 0.53333 | 779.3106 | 11 | 8.1667 | Feeder #4A | 25 | 2020-10-02 | Feeders tripped due to IPOS losing steam for their vaporizer
Feeder #4A (13 Kv) | 1499464.5 | 1521248.3125 | 0 | 2 | 2.3333 | 4717.4164 | 10 | 9.35 | Feeder #1A | 114 | 2020-10-14 | IPOS had issues with their export pump resulting in a loss of propane supply
Feeder #5A (13 Kv) | 3620000 | 3715000 | 0 | 1 | 0.033333 | 162.1936 | 4 | 3.5 | Feeder #2A | 2 | 2020-10-14 | IPOS had issues with their export pump resulting in a loss of propane supply
Feeder #6A (13 Kv) | 2085241 | 2168271 | 0 | 1 | 1.9 | 5338.8464 | 5 | 8.6 | Feeder #3A | 2 | 2020-10-14 | IPOS had issues with their export pump resulting in a loss of propane supply
Feeder #9A (13 Kv) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Feeder #4A | 115 | 2020-10-14 | IPOS had issues with their export pump resulting in a loss of propane supply
Feeder #6B (24 Kv) | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4.4333 | Feeder #5A | 2 | 2020-10-14 | IPOS had issues with their export pump resulting in a loss of propane supply
Feeder #8B (24 Kv) | 7030357 | 6211912.25 | 0 | 1 | 0.033333 | 314.9943 | 4 | 4.4333 | Feeder #6A | 114 | 2020-10-14 | IPOS had issues with their export pump resulting in a loss of propane supply
Feeder #9B(24Kv) | 0 | 3441006.4605 | 0 | 0 | 0 | 0 | 2 | 4.9333 | Feeder #8B | 2 | 2020-10-14 | IPOS had issues with their export pump resulting in a loss of propane supply
Feeder #10A(24Kv) | 1859330 | 1511816.6667 | 0 | 0 | 0 | 0 | 0 | 0 | Feeder #10A | 124 | 2020-10-14 | IPOS had issues with their export pump resulting in a loss of propane supply
Feeder #10B(24Kv) | 1507122.75 | 1518504.5 | 0 | 2 | 2.1833 | 4435.8013 | 17 | 12.6667 | Feeder #10B | 115 | 2020-10-14 | IPOS had issues with their export pump resulting in a loss of propane supply
TOTALS | 22783668.5 | 25515127.7047 | 0 | 15 | 11.9 | 30425.699 | 85 | 86.3333 | Feeder #2A | 142 | 2020-10-14 | Due to insufficient load generation
[9 empty] | Feeder #2A | 5 | 2020-10-29 | Several Aggreko units tripped due to trip ignition failure
[9 empty] | Feeder #3A | 6 | 2020-10-29 | Several Aggreko units tripped due to trip ignition failure
[9 empty] | Feeder #10A | 7 | 2020-10-29 | Several Aggreko units tripped due to trip ignition failure
[9 empty] | Feeder #10B | 10 | 2020-10-29 | Several Aggreko units tripped due to trip ignition failure
0
0
0
0
0

## PR-Pag6
October - 2020
Power - Water Units Outages
|  | TOTAL NUMBER OF OUTAGES |  |  |  | PLANNED OUTAGES |  |  |  | FORCED OUTAGES
| This Month | FYTD | This Month | FYTD | This Month | FYTD | Duration | FYTD | This Month | FYTD | Duration | FYTD
Unit | Outages | Outages | Hours | Hours | Outages | Outages | Hours | Hours | Outages | Outages | Hours | Hours
Unit 10ST | 1 | 4 | 744 | 2952 | 1 | 4 | 744 | 2952 | 0 | 0 | 0 | 0
Unit 11ST | 1 | 4 | 744 | 2952 | 1 | 4 | 744 | 2952 | 0 | 0 | 0 | 0
Unit11BLR | 1 | 4 | 744 | 2952 | 1 | 4 | 744 | 2952 | 0 | 0 | 0 | 0
Unit 16 | 0 | 0 | 744 | 2952 | 0 | 0 | 744 | 2952 | 0 | 0 | 0 | 0
Unit 17 | 0 | 4 | 0 | 26.65 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 26.65
Unit 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Unit 20 | 1 | 4 | 744 | 2952 | 1 | 4 | 744 | 2952 | 0 | 0 | 0 | 0
Aggreko | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HRSG 21 | 1 | 4 | 744 | 2952 | 1 | 4 | 744 | 2952 | 0 | 0 | 0 | 0
HRSG 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTALS | 5 | 24 |  |  | 5 |  |  |  | 0 | 2
Plant Power Distribution
|  |  | This Month | FYTD | FYTD |  |  |  | Peak and Min. Load Data
|  |  | KWH | KWH | AVG. | [5 empty] | FYTD
Total 13KV Feeders |  |  | 12386858.75 | 51327551.31 | 12831887.8275 |  |  |  |  | This Month | AVG.
Total 24KV Feeders |  |  | 10396809.75 | 42339129.921 | 10584782.4803 |  |  | Peak Load (KW) |  | 39340 | 40570
Feeder Totals |  |  | 22783668.5 | 93666681.231 | 23416670.3078 |  |  | Day |  | Saturday
Total Generation |  |  | 24404586 | 100165151.5 | 25041287.875 |  |  | Date |  | 2020-10-10
T1,T3,T4, T5, T6, T7 Available |  |  | 9737195 | 139249355 | 34812338.75 |  |  | Hour |  | 18:39
T1&T3&T4&T5&T6&T7 Losses* |  |  | 237737.5 | 903076.769 | 225769.1922
Net Distributed |  |  | 24166848.5 | 99262074.731 | 24815518.6828 |  |  | Min. Load (KW) |  | 25910 | 26397.5
Line Department |  |  |  | 0 | 0 |  |  | Day |  | Thursday
Water Department |  |  |  | 0 | 0 |  |  | Date |  | 2020-10-29
Power Plant Services |  |  |  | 0 | 0 |  |  | Hour |  | 3:00
Administration & General |  |  |  | 0 | 0
Plant Station Service |  |  |  | 0 | 0
Net Available from Bus |  |  |  | 0 | 0
Wapa KWH From Dist |  |  |  | 0 | 0 |  | * meters under review
SwitchGear Bkr1 SS |  |  | 1076282.5 | 4346826.5 | 1086706.625
SwitchGear Bkr3 SS |  |  | 302817.5 | 1213167 | 303291.75
Total Station Service Power |  |  | 1273462 | 5577693.5 | 1394423.375
Net KWH Available for Sale |  |  | 22785708.5 | 93684381.231 | 23421095.3078
Plant Unaccountable |  |  | 0 | 0 | 0
0
0
0
0
0

## PR-Pag7
October - 2020
|  |  | Fuel Allocation | BBLS
|  |  | Propane Fuel For Power | 87289.9286
|  |  | Propane Fuel For Water | 0
|  |  | No 2 Fuel For Power | 1935.0103
|  |  | No 2 Fuel For Water | 0
|  |  | O&M Factor for Water | 0
Power Boilers
11
TPBSFC
BLR11FUELCOST
0 |  | GT Fuel Allocation
HP Stm from WHB
GTFCAE
WHBHPSTMCOST
Combined Cycle |  | 0
WHB, 16. 17. 20
TGTFC |  |  |  |  | Electrc Power
GEN1617FUELCOST |  |  |  |  | Generation
1804814.6582 |  |  |  |  | TOTFUELCOSTPWR
|  |  | Gas Turbine |  | 3315497.8093
Power Allocation
Simple Cycle |  |  | GTFCA
GEN161720ADJFCOST
GEN 19 FUELCOST |  |  | 1804814.6582
88884.4036
RO Water
DIESEL |  |  |  |  | Production Cost
Emergency Gen.
DIESEL_EMER. |  |  |  |  | 149650.5959
0
*Note: The fuel prices in this report are an estimation
Cost Calculated at:
| 69.2813 | per BBL for No. 2
| 38.1612 | per BBL for Propane

## PR-Pag8
October - 2020
Fuel Allocations
Fuel Summary |  |  |  | ITEM | Amount | FYTD
ITEM | Propane | No2 BBLS
|  |  |  | Electric Power Generation | 3315497.8093 | 14336018.7894
Inventory-Beginning of Month |  | 40409.5766 |  | Water Production* | 149650.5959 | 631091.8443
Received During Month |  | 0 |  | Total #2 Fuel Cost | 134059.983 | 2361492.1684
Consumed During Month |  | 1935.0103 |  | BBLS Propane for Power | 87289.9286 | 330759.5952
Inventory-End of Month |  | 38474.5663 |  | BBLS Propane for Water | 0 | 0
Calorific Value (BTU/GAL) | 91647 | 136999.0879 |  | BBLS No. 2 for Power | 1935.0103 | 33448.1166
|  |  |  | BBLS No.2 for Water | 0 | 0
|  |  |  | Propane BBL Cost | 38.1612
End of Month- Fuel in Tanks |  |  |  | No. 2 BBL Cost | 69.2813
|  | No 2 BBLS |  | * Note: Includes RO Electric Usage
|  |  |  | No. 2 Oil Used | This Month | FYTD
Tank 1 |  | 0 |  | No. 2 Units | BBLS No. 2 | BBLS No. 2
Tank 2 |  | 0
Tank 3 |  | 4451.44 |  | Unit 11 | 0 | 0
Tank 4 |  | 4037.85 |  | Unit 16 | 0 | 0
Tank 5 |  | 28860.59 |  | Unit 17 | 652.0604 | 9202.9399
Tank 6 |  | 1124.68 |  | Unit 19 | 1282.9499 | 24245.1767
Tank 7 |  |  |  | Unit 20 | 0 | 0
TOTALS | 0 | 38474.5663 |  | Diesel Emergency | 0 | 0
|  |  |  | Total No. 2 Consumed | 1935.0103 | 33448.1166
Fuel Shipments |  |  |  | Propane Used | This Month | FYTD
|  | No2 | No2 | Propane Units | Gals | Gals
|  | Date | BBLS | Unit 16 | 0 | 0
|  |  |  | Unit 17 | 1936648.7771 | 7378016.4629
|  |  |  | Unit 20 | 0 | 0
|  |  |  | Aggreko | 1729528.2229 | 6513886.5371
|  |  |  | Total Propane Consumed | 3666177 | 13891903
TOTAL SHIPMENTS |  |  | 0
|  |  |  | Tank Fuel / Metered Fuel | Ratio
Used Oil recovered | 0 | Bbls
|  |  |  | No. 2 | 0.99936
|  |  |  | Propane | 0.97071
Ratio 0.95 to 1.05 acceptable
0
0
0
0
0

## PR-Pag9
October - 2020

## PR-Pag10
October - 2020

## PR-Pag11
October - 2020