## DataBase
FISCAL YEAR 2020-2021
|  | 31 | 31 | 30 | 31 | 30 | 31 | 31 | 28 | 31 | 30 | 31 | 0
|  | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY | JUN | FYTD | FYTD-AVG
Item | Index | 7 | 8 | 9 | 10 | 12 | 12 | 13 | 14 | 15 | 16 | 17 | 18
Total System Generation |  | 25719.9895 | 25797.0635 | 24243.5125 | 24404.586 | 22938.64 | 22207.3064 | 21720.8868 | 19883.8923 |  |  |  |  | 186915.877 | 23364.4846
Gross Power Generation |  | 25075.95 | 25132.08 | 23591.11 | 23735.79 | 22338.04 | 21615.68 | 21130.86 | 19245.18 |  |  |  |  | 181864.69 | 22733.0863
Gross Water Production |  | 90987.3333 | 89121.8333 | 82706.1667 | 88049.8333 | 87245.3333 | 88737.3333 | 98485.5 | 87791.8333 |  |  |  |  | 713125.1667 | 89140.6458
System Load Factor |  | 82.05% | 80.83% | 81.77% | 81.1% | 78.74% | 77.83% | 74.31% | 80.67% |  |  |  |  | 637.3% | 79.66%
Total No. 6 Fuel Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Total No. 2 Fuel Cost |  | 426605.2954 | 639765.748 | 1161061.1421 | 134059.983 | 151618.4179 | 142478.9617 | 287462.368 | 111350.8443 |  |  |  |  | 3054402.7603 | 381800.345
Total Propane Cost |  | 3453706.8756 | 3267490.988 | 2553332.1795 | 3331088.4222 | 3278983.919 | 3530353.84 | 4147376.4276 | 3759547.2414 |  |  |  |  | 27321879.8933 | 3415234.9867
Power Fuel Cost (Internal) |  | 0.15474 | 0.15547 | 0.15745 | 0.14599 | 0.15358 | 0.16992 | 0.20987 | 0.20114 |  |  |  |  | 1.3482 | 0.16852
Power Fuel Cost (to bus) |  | 0.16018 | 0.16268 | 0.16406 | 0.15209 | 0.16122 | 0.17624 | 0.22441 | 0.21123 |  |  |  |  | 1.4121 | 0.17651
Water Fuel Cost (Internal) |  | 1.8354 | 1.8234 | 1.8371 | 1.6996 | 1.7806 | 1.9862 | 2.4964 | 2.3764 |  |  |  |  | 15.8352 | 1.9794
Water Fuel Cost (to Distribution |  | 1.872 | 1.8621 | 1.8651 | 1.7235 | 1.812 | 2.0222 | 2.5423 | 2.4197 |  |  |  |  | 16.1189 | 2.0149
Total Power Fuel Cost |  | 3713314.5045 | 3744752.5614 | 3562453.9143 | 3315497.8093 | 3275251.6783 | 3496583.1529 | 4188975.5048 | 3662267.9831 |  |  |  |  | 28959097.1085 | 3619887.1386
Total Water Fuel Cost |  | 166997.6665 | 162504.1747 | 151939.4073 | 149650.5959 | 155350.6585 | 176249.6488 | 245863.2908 | 208630.1026 |  |  |  |  | 1417185.5451 | 177148.1931
No. 6 Fuel Consumed |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
No. 2 Fuel Consumed |  | 5520.1249 | 9234.3241 | 16758.6572 | 1935.0103 | 2188.4473 | 2056.614 | 4149.3782 | 1607.2953 |  |  |  |  | 43449.8514 | 5431.2314
No. 6 Fuel Received |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
No. 2 Fuel Received |  | 0 | 32182.12 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 32182.12 | 32182.12
EOM No. 6 Fuel On Hand |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
EOM No. 2 Fuel On Hand(based on 2000Bbl/day Consumption) |  | 17.1102 | 28.5841 | 20.2048 | 19.2373 | 18.1431 | 17.1148 | 15.0401 | 14.2364 |  |  |  |  | 149.6707 | 18.7088
Plant Water Use ( Internal) |  | 15419.311 | 1905.8303 | 2090.0527 | 1555.6764 | 1504.9232 | 1581.128 | 2214.499 | 1406.5682 |  |  |  |  | 27677.9888 | 3459.7486
Plant Power Use (Internal) |  | 205429.6386 | 202269.0761 | 191866.8631 | 185910.594 | 190442.1069 | 220693.5206 | 312429.1532 | 277296.7445 |  |  |  |  | 1786337.6971 | 223292.2121
Heat Rates BTU/KWH | [13 empty] | 0 | 0
(Net Energy in KWH Produced) | [13 empty] | 0 | 0
Units | [13 empty] | 0 | 0
Combined Cycle-Units 10,16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Combined Cycle-Units 11,16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 10-Steam (10 MW) |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  |  |  | 0 | 0
Unit 11-Steam (21 MW) |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  |  |  | 0 | 0
Unit 16-Gas Turbine (23 MW) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 17-Gas Turbine (20.3 MW) |  | 19723.3655 | 19377.4218 | 19918.1643 | 20433.9315 | 20902.8681 | 21861.1136 | 20842.1156 | 18459.5883 |  |  |  |  | 161518.5687 | 20189.8211
Unit 19-Gas Turbine (24 MW) |  | 31163.4711 | 25705.1735 | 19292.4251 | 22369.8317 | 21548.3601 | 24977.4508 | 21940.2019 | 18210.4459 |  |  |  |  | 185207.3601 | 23150.92
Unit 20_Gas Turbine (24 MW) |  | 0 | 0 | 0 | 0 | 0 | 41467.1816 | 20598.0852 | 21478.4125 |  |  |  |  | 83543.6793 | 27847.8931
Aggreko |  | 10887.2856 | 10962.7384 | 10998.875 | 10904.2078 | 10898.0236 | 10911.9193 | 11041.1381 | 11140.594 |  |  |  |  | 87744.7819 | 10968.0977
Total Plant . |  | 15100.2454 | 15206.0874 | 15197.1983 | 14624.6701 | 14782.9218 | 15044.4226 | 15397.26 | 14863.9622 |  |  |  |  | 120216.7679 | 15027.096
Desal Performance Ratios | [13 empty] | 0 | 0
IDE3 (1.25MGD) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE4 (.55MGD) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE5 (0.55MGD) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE9 (1.3MGD) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit Availability Percent | [13 empty] | 0 | 0
Unit 10 | [13 empty] | 0% | 0% | bar: 7 to 14
Unit 11 | [13 empty] | 0% | 0% | bar: 7 to 14
Unit 16 | [13 empty] | 0% | 0% | bar: 7 to 14
Unit 17 |  | 100% | 100% | 96.3% | 100% | 100% | 100% | 100% | 100% |  |  |  |  | 796.3% | 99.54%
Unit 19 |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  |  |  |  | 800% | 100%
Unit 20 |  | 0% | 0% | 0% | 0% | 0% | 2.78% | 100% | 100% |  |  |  |  | 202.8% | 25.35%
Aggreko |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  |  |  |  | 800% | 100%
IDE 3 |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  |  |  |  | 800% | 100%
IDE 4 | [13 empty] | 0% | 0% | bar: 7 to 14
IDE 5 | [13 empty] | 0% | 0% | bar: 7 to 14
IDE 9 |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  |  |  |  | 800% | 100%
HRSG 21 | [13 empty] | 0% | 0% | bar: 7 to 14
HRSG 24 |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  |  |  |  | 800% | 100%
Pag2 | [13 empty] | 0 | 0
Item | [13 empty] | 0 | 0
Steam Turbine Generation |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Gas Turbine Generation |  | 25075950 | 25132080 | 23591110 | 23735790 | 22338040 | 21615680 | 21130860 | 19245180 |  |  |  |  | 181864690 | 22733086.25
Diesel Generation |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Total Generation |  | 25075950 | 25132080 | 23591110 | 23735790 | 22338040 | 21615680 | 21130860 | 19245180 |  |  |  |  | 181864690 | 22733086.25
IPP1 |  | 644039.5 | 664983.5 | 652402.5 | 668796 | 600600 | 591626.406 | 590026.844 | 638712.25 |  |  |  |  | 5051187 | 631398.375
Total System Generation |  | 25719989.5 | 25797063.5 | 24243512.5 | 24404586 | 22938640 | 22207306.406 | 21720886.844 | 19883892.25
Steam Station Power |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Gas Turbine Station Power |  | 45390 | 45350 | 49610 | 36910 | 35210 | 62750 | 103800 | 115400 |  |  |  |  | 494420 | 61802.5
Total Gen. Plant Station Power |  | 45390 | 45350 | 49610 | 36910 | 35210 | 62750 | 103800 | 115400 |  |  |  |  | 494420 | 61802.5
Total Service / Gross Output |  | 0.181% | 0.1804% | 0.2103% | 0.1555% | 0.1576% | 0.2903% | 0.4912% | 0.5996% |  |  |  |  | 2.266% | 0.2833%
Operating Hours | [13 empty] | 0 | 0
Unit 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 11 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 17 |  | 739.5 | 722.8 | 610.5 | 728.2 | 704.3 | 727.4 | 414.1 | 80.2 |  |  |  |  | 4727 | 590.875
Unit 19 |  | 180.1 | 242.4 | 287.9 | 41.9 | 58.7 | 29.4 | 86.3 | 29 |  |  |  |  | 955.7 | 119.4625
Unit 20 |  | 0 | 0 | 0 | 0 | 0 | 19.6 | 401.3 | 592.8 |  |  |  |  | 1013.7 | 337.9
Aggreko |  | 713.003 | 697.0245 | 639.6298 | 741.0772 | 691.7374 | 728.6257 | 0 | 607.523 |  |  |  |  | 4818.6205 | 688.3744
Diesel Generation(Emergency) |  | 1 | 3 | 0 | 3 | 1 | 1 | 1 | 2 |  |  |  |  | 12 | 1.7143
Unit Average Loading | [13 empty] | 0 | 0
(KWH / Operating Hours) | [13 empty] | 0 | 0
Unit 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 11 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 17 |  | 13623.1508 | 13655.7831 | 13025.7166 | 12180.1154 | 11559.9035 | 10267.5282 | 10396.6192 | 10720.6983 |  |  |  |  | 95429.5149 | 11928.6894
Unit 19 |  | 4553.0261 | 6600.6601 | 11774.9218 | 7875.895 | 8517.8876 | 7142.8571 | 7995.365 | 10000 |  |  |  |  | 64460.6127 | 8057.5766
Unit 20 |  | 0 | 0 | 0 | 0 | 0 | 7677.551 | 11037.9267 | 10331.444 |  |  |  |  | 29046.9218 | 9682.3073
Aggreko |  | 19890 | 19600 | 19150 | 19615 | 19800 | 18921.375 | 0 | 19704.4402 |  |  |  |  | 136680.8152 | 19525.8307
Diesel |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Utilization Factor | [13 empty] | 0 | 0
Unit 10 | [13 empty] | 0% | 0% | bar: 7 to 14
Unit 11 | [13 empty] | 0% | 0% | bar: 7 to 14
Unit 16 | [13 empty] | 0% | 0% | bar: 7 to 14
Unit 17 |  | 62.21% | 62.36% | 59.48% | 55.62% | 52.78% | 46.88% | 47.47% | 48.95% |  |  |  |  | 435.8% | 54.47%
Unit 19 |  | 18.58% | 26.94% | 48.06% | 32.15% | 34.77% | 29.15% | 32.63% | 40.82% |  |  |  |  | 263.1% | 32.89%
Unit 20 |  | 0% | 0% | 0% | 0% | 0% | 31.34% | 45.05% | 42.17% |  |  |  |  | 118.6% | 39.52%
Aggreko |  | 99.45% | 98% | 95.75% | 98.08% | 99% | 94.61% | 0% | 98.52%
Diesel | 1 | [12 empty] | 0% | 0% | bar: 7 to 14
Unit Output KW | 2 | [12 empty] | 0 | 0
Unit 10 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 11 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 17 | 6 | 10074320 | 9870400 | 7952200 | 8869560 | 8141640 | 7468600 | 4305240 | 859800 |  |  |  |  | 57541760 | 7192720
Unit 19 | 7 | 820000 | 1600000 | 3390000 | 330000 | 500000 | 210000 | 690000 | 290000 |  |  |  |  | 7830000 | 978750
Unit 20 | 8 | 0 | 0 | 0 | 0 | 0 | 150480 | 4429520 | 6124480 |  |  |  |  | 10704480 | 3568160
Aggreko |  | 14181630 | 13661680 | 12248910 | 14536230 | 13696400 | 13786600 | 11706100 | 11970900 |  |  |  |  | 105788450 | 13223556.25
Diesel |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
TOTAL | 9 | 25075950 | 25132080 | 23591110 | 23735790 | 22338040 | 21615680 | 21130860 | 19245180 |  |  |  |  | 181864690 | 22733086.25
Unit Station Service Power | [13 empty] | 0 | 0
Unit 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 11 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 17 |  | 2370 | 3560 | 6150 | 2820 | 2490 | 2640 | 14000 | 23790 |  |  |  |  | 57820 | 7227.5
Unit 19 |  | 35520 | 34800 | 36960 | 27680 | 27120 | 27440 | 28160 | 22800 |  |  |  |  | 240480 | 30060
Unit 20 |  | 7500 | 6990 | 6500 | 6410 | 5600 | 32670 | 61640 | 68810 |  |  |  |  | 196120 | 24515
Aggreko |  | 260 | 450 | 2350 | 670 | 230 | 400 | 470 | 790 |  |  |  |  | 5620 | 702.5
Diesel |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
TOTAL |  | 45390 | 45350 | 49610 | 36910 | 35210 | 63150 | 104270 | 116190 |  |  |  |  | 496080 | 62010
pag3 | [13 empty] | 0 | 0
BOILERS/STM. TURBINES | [13 empty] | 0 | 0
[14 empty] | 0 | 0
SS10 Plant Aux. Trans 480V |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
SS10 Unit Aux.. Trans 480V |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
[14 empty] | 0 | 0
Unit 10 Total Station Power |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
SS11 Plant Aux. Trans 480V |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
SS11 Unit Aux.. Trans 480V |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
[14 empty] | 0 | 0
Unit 11 Net Total Station Power |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
HRSG 21 Station Power |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
HRSG 24 Station Power |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
WHB Net Station Power |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
TOTAL BOILERS / STM TURBINES |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
GAS TURBINE | [13 empty] | 0 | 0
[14 empty] | 0 | 0
Plant SS | [13 empty] | 0 | 0
Unit 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 17 |  | 30 | 980 | 4410 | 780 | 690 | 600 | 12920 | 23610 |  |  |  |  | 44020 | 5502.5
Unit 19 |  | 35520 | 34800 | 36960 | 27680 | 27120 | 27440 | 28160 | 22800 |  |  |  |  | 240480 | 30060
Unit 20 |  | 0 | 5490 | 6500 | 6410 | 5600 | 32670 | 61640 | 68810 |  |  |  |  | 187120 | 26731.4286
|  | 260 | 450 | 2350 | 670 | 230 | 400 | 470 | 790 |  |  |  |  | 5620 | 702.5
Unit SS | [13 empty] | 0 | 0
Unit 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 17 |  | 2340 | 2580 | 1740 | 2040 | 1800 | 2040 | 1080 | 180 |  |  |  |  | 13800 | 1725
Unit 19 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 20 |  | 7500 | 1500 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 9000 | 4500
|  | 9840 | 4080 | 1740 | 2040 | 1800 | 2040 | 1080 | 180 |  |  |  |  | 22800 | 2850
Plant IDE pumpage | [13 empty] | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
[14 empty] | 0 | 0
Total |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
TOTAL GAS TURBINES |  | 45650 | 45800 | 51960 | 37580 | 35440 | 63150 | 104270 | 116190 |  |  |  |  | 500040 | 62505
STX. EMERGENCY DIESEL | [13 empty] | 0 | 0
[14 empty] | 0 | 0
Diesel |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
TOTAL DIESEL |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
WATER PLANTS | [13 empty] | 0 | 0
[14 empty] | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Intake Pump A |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Intake Pump B |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Intake Pump C |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE Intake Pumps A&B+Chloropac |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
RO Plant |  | 458594 | 477312 | 395292 | 448162 | 427195 | 459956 | 515267 | 427483 |  |  |  |  | 3609261 | 451157.625
UPW Electricity |  | 17911 | 17174 | 15510 | 15316 | 14254.62 | 14855 | 15579.12 | 13681.13 |  |  |  |  | 124280.87 | 15535.1088
RO ANNEX Electricity |  | 620604 | 567940 | 569716 | 576924 | 584356 | 577324 | 656208 | 609776 |  |  |  |  | 4762848 | 595356
TOTAL WATER PLANTS |  | 1097109 | 1062426 | 980518 | 1040402 | 1025805.62 | 1052135 | 1187054.12 | 1050940.13 |  |  |  |  | 8496389.87 | 1062048.7338
OTHERS | [13 empty] | 0 | 0
[14 empty] | 0 | 0
Station Service Shops |  | 25440 | 31680 | 29640 | 27480 | 26160 | 25800 | 25320 | 26640 |  |  |  |  | 218160 | 27270
Station Service Office | [13 empty] | 0 | 0
Fuel Tanks SS | [13 empty] | 0 | 0
Switch Yard SS |  | 159360 | 161120 | 156480 | 168000 | 152640 | 157760 | 172000 | 166240 |  |  |  |  | 1293600 | 161700
|  | 14: 591 | 591 | 591
|  | 14: 18052 | 18052 | 18052
TOTAL OTHERS |  | 184800 | 192800 | 186120 | 195480 | 178800 | 183560 | 197320 | 211523 |  |  |  |  | 1530403 | 191300.375
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
SwitchGear Bkr1 SS |  | 1126712.5 | 1097708.5 | 1046123 | 1076282.5 | 1059253 | 1087062.87 | 1218442.13 | 1079256.5 |  |  |  |  | 8790841 | 1098855.125
SwitchGear Bkr3 SS |  | 301288.25 | 306636 | 302425.25 | 302817.5 | 284381.05 | 317414.7 | 369246.25 | 361867 |  |  |  |  | 2546076 | 318259.5
[14 empty] | 0 | 0
Total |  | 1428000.75 | 1404344.5 | 1348548.25 | 1379100 | 1343634.05 | 1404477.57 | 1587688.38 | 1441123.5 |  |  |  |  | 11336917 | 1417114.625
Total SS from GAC |  | 9840 | 4080 | 1740 | 2040 | 1800 | 2040 | 1080 | 180 |  |  |  |  | 22800 | 2850
Total Station Service Power |  | 1327559 | 1301026 | 1218598 | 1273462 | 1240045.62 | 1298845 | 1488644.12 | 1378653.13 |  |  |  |  | 10526832.87 | 1315854.1088
Total Unit #11 SS (Not Plant) | [13 empty] | 0 | 0
Total Unit #10 SS (Not Plant) | [13 empty] | 0 | 0
[14 empty] | 0 | 0
TOTAL STATION POWER |  | 1327559 | 1301026 | 1218598 | 1273462 | 1240045.62 | 1298845 | 1488644.12 | 1378653.13 |  |  |  |  | 10526832.87 | 1315854.1088
KWH | [13 empty] | 0
ENERGY DISTRIBUTION | [13 empty] | 0
0
0
0
0
GROSS ENERGY DISTRIBUTION | [13 empty] | 0
Gross Electric Energy Produced |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
Gross Energy Used in Water Plants |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
PLANT TOTAL GROSS ENERGY USED |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
0
NET ENERGY DISTRIBUTION | [13 empty] | 0
Net Electricity to Distribution |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
Net Energy used on water to distribution |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
PLANT TOTAL NET ENERGY USED |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
0
Plant Service / Gross Output |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
0
BTU's | [13 empty] | 0
Fuel No. 2 Consumed (BTU's) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
Fuel No. 6 Consumed (BTU's) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
TOTAL ENERGY IN FUEL |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
0
GROSS ENERGY DISTRIBUTION | [13 empty] | 0
Gross Electric Energy Produced |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
Gross Energy Used in Water Plants |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
PLANT TOTAL GROSS ENERGY USED |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
0
NET ENERGY DISTRIBUTION | [13 empty] | 0
Net Electricity to Distribution |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
Net Energy used on water to distribution |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
PLANT TOTAL NET ENERGY USED |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
0
Plant Service / NET Output |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
0
EFFICIENCY | [13 empty] | 0
0
Gross Efficiency | [13 empty] | 0
Electric Generating Plant Only |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
Water Desalination Plant only |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
Combined Generating and Water Plant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
0
Net Efficiency | [13 empty] | 0
Electric Generating Plant Only |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
Water Desalination Plant only |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
Combined Generating and Water Plant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
0
Heat Rates BTU/KWH | [13 empty] | 0
0
Gross Heat Rate | [13 empty] | 0
Electric Generating Plant Only |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
Water Desalination Plant only |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
Combined Generating and Water Plant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
0
Net Heat Rate | [13 empty] | 0
Electric Generating Plant Only |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
Water Desalination Plant only |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
Combined Generating and Water Plant |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
[14 empty] | 0 | 0
pag4 | [13 empty] | 0 | 0
Desalination Plants Summary | [13 empty] | 0 | 0
Unit Service HRS | [13 empty] | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit Output GALS | [13 empty] | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
From TC |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
RO WAPA Meter |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
RO 7Seas water Meter 1 |  | 37516000 | 39683000 | 32676000 | 37374000 | 36186000 | 38640000 | 42643000 | 35802000 |  |  |  |  | 300520000 | 37565000
RO 7Seas water Meter 2 |  | 37390000 | 39542000 | 32563000 | 37249000 | 36082000 | 38582000 | 42548000 | 35729000 |  |  |  |  | 299685000 | 37460625
RO Meter Average |  | 37453000 | 39612500 | 32619500 | 37311500 | 36134000 | 38611000 | 42595500 | 35765500 |  |  |  |  | 300102500 | 37512812.5
RO 7Seas ANNEXwater Meter 1 |  | 53489000 | 49507000 | 50040000 | 50630000 | 51000000 | 50089000 | 55786000 | 51969000
RO 7Seas ANNEX water Meter 2 |  | 53630000 | 49527000 | 50154000 | 50942000 | 51229000 | 50195000 | 56097000 | 52176000
RO 7Seas ANNEX water Meter 3 |  | 53484000 | 49494000 | 50066000 | 50643000 | 51105000 | 50095000 | 55787000 | 51934000
RO Meter Average |  | 53534333.3333 | 49509333.3333 | 50086666.6667 | 50738333.3333 | 51111333.3333 | 50126333.3333 | 55890000 | 52026333.3333 |  |  |  |  | 413022666.6667 | 51627833.3333
STX TOTALS |  | 90987333.3333 | 89121833.3333 | 82706166.6667 | 88049833.3333 | 87245333.3333 | 88737333.3333 | 98485500 | 87791833.3333 |  |  |  |  | 713125166.6667 | 89140645.8333
Unit Cond LBS | [13 empty] | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
STX TOTALS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit LP Steam LBS | [13 empty] | 0 | 0
[14 empty] | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
STX TOTALS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit HP Steam LBS | [13 empty] | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
STT TOTALS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit Utilization Factor Percent | [13 empty] | 0% | 0%
IDE 3 | [13 empty] | 0% | 0% | bar: 7 to 14
IDE 4 | [13 empty] | 0% | 0% | bar: 7 to 14
IDE 5 | [13 empty] | 0% | 0% | bar: 7 to 14
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0% | 0%
Boilers Summary | [13 empty] | 0 | 0
Service Hrs | [13 empty] | 0 | 0
WHB 21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
HRSG 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Boiler 11 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
This Month Gals | [13 empty] | 0 | 0
WHB 21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
HRSG 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Boiler 11 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
TOTALS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
This Month LP STM LBS | [13 empty] | 0 | 0
WHB 21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
HRSG 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Boiler 11 | [13 empty] | 0 | 0
TOTALS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
This Month HP STM LBS | [13 empty] | 0 | 0
WHB 21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
HRSG 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Boiler 11 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
TOTALS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Water Distribution | [13 empty] | 0 | 0
Total Water Produced |  | 90987333.3333 | 89121833.3333 | 82706166.6667 | 88049833.3333 | 87245333.3333 | 88737333.3333 | 98485500 | 87791833.3333 |  |  |  |  | 713125166.6667 | 89140645.8333
Total to Distribution Tank |  | 89206406.6667 | 87271346.6667 | 81464380 | 86830084.6667 | 85733049.6667 | 87158109.6667 | 96708970.3333 | 86222022.3333 |  |  |  |  | 700594370 | 87574296.25
Apparent Station Use |  | 1780926.6667 | 1850486.6667 | 1241786.6667 | 1219748.6667 | 1512283.6667 | 1579223.6667 | 1776529.6667 | 1569811 |  |  |  |  | 12530796.6667 | 1566349.5833
Water to day Tank (Booster) Plus UPW Product |  | 1151333.3333 | 1244333.3333 | 1259000 | 1001333.3333 | 907333.3333 | 983333.3333 | 1165666.6667 | 889333.3333 |  |  |  |  | 8601666.6667 | 1075208.3333
Water to the Demineralizer(regen) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Boilers Make Up |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 16 Noxwater |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 17 Noxwater |  | 8237911.2549 | 813283.4473 | 756803.4668 | 825476.5625 | 760796.3867 | 731756.3477 | 414203.125 | 51999.1455 |  |  |  |  | 12592229.7363 | 1574028.717
Unit 19 Noxwater |  | 136276.123 | 214627.1973 | 360488.5254 | 39235.8398 | 57672.3633 | 27504.3945 | 86946.5332 | 25788.1718 |  |  |  |  | 948539.1483 | 118567.3935
Unit 20 Noxwater |  | 0 | 0 | 0 | 0 | 0 | 15998.0469 | 345412.5977 | 479598.5107 |  |  |  |  | 841009.1553 | 280336.3851
Total Wtr to NOX |  | 1007500 | 1094100 | 1093700 | 849900 | 812300 | 873400 | 1034200 | 796200 |  |  |  |  | 7561300 | 945162.5
Station Wtr Warehouse & Eng. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Plant Service Water |  | 26900 | 17300 | 20400 | 50600 | 26700 | 20800 | 40500 | 34500 |  |  |  |  | 237700 | 29712.5
Admin. Off. Water |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
WTR to Fire Hydrants |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Total Water Used |  | 1780926.6667 | 1850486.6667 | 1241786.6667 | 1219748.6667 | 1512283.6667 | 1579223.6667 | 1776529.6667 | 1569811 |  |  |  |  | 12530796.6667 | 1566349.5833
Unaccountable Water |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Steam Summary | [13 empty] | 0 | 0
LP Steam LBS | [13 empty] | 0 | 0
Total Steam Produced |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
From Steam Turbine 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
From Steam Turbine 11 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
[14 empty] | 0 | 0
HP STM to IDE's Ejectors | [13 empty] | 0 | 0
LP STM to IDE's Process |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Used Steam for Production |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
[14 empty] | 0 | 0
Others uses & Deareator |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
HP Steam LBS | [13 empty] | 0 | 0
Total Steam Produced |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
To Steam Turbine 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
To Steam Turbine 11 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
From Steam Turbines |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
HP STM to IDE's Ejectors |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
LP STM to IDE's Process | [13 empty] | 0 | 0
Used Steam for Production |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
[14 empty] | 0 | 0
Others uses & Deareator |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Boiler MUF from MUF Meters |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Boiler MUF from Desal Unit HPSTM Meters |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Boilers MUF per Desal Design Quantities |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
LPSTM to Desal/Condensate Return | [13 empty] | 0% | 0% | bar: 7 to 14
Boiler 10 MUF/HPSTM Generated | [13 empty] | 0% | 0%
Boiler 11 MUF/HPSTM Generated |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  |  |  | 0% | 0%
WHB MUF / HP & LPSTM Generated |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  |  |  | 0 | 0
[14 empty] | 0% | 0%
pag5 | [13 empty] | 0% | 0%
Feeder KWH | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 1360494.62 | 1358974.88 | 1203228 | 1236634 | 1144082 | 1184869.5 | 1129771.5 | 1075595.5 |  |  |  |  | 9693650 | 1211706.25
Feeder # 2 (13 Kv) |  | 3241831.56 | 3157129.75 | 2883075 | 2859160.25 | 2675297.25 | 2639121 | 2549364.06 | 2331014.69 |  |  |  |  | 22335993.56 | 2791999.195
Feeder # 3 (13(Kv) |  | 1111674 | 1126770 | 1084143 | 1086359 | 969113 | 1013913 | 945235 | 858463 |  |  |  |  | 8195670 | 1024458.75
Feeder # 4 (13 Kv) |  | 1542316.75 | 1558387 | 1484825 | 1499464.5 | 1392114.5 | 1357023.75 | 1284643.25 | 1184914 |  |  |  |  | 11303688.75 | 1412961.0938
Feeder # 5 (13 Kv) |  | 3890000 | 3720000 | 3630000 | 3620000 | 3230000 | 3090000 | 2920000 | 2700000 |  |  |  |  | 26800000 | 3350000
Feeder # 6 (13 Kv) |  | 2272777 | 2244390 | 2070676 | 2085241 | 1905874 | 1980862 | 1833886 | 1668356 |  |  |  |  | 16062062 | 2007757.75
Feeder # 9A (13 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 6B (24 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 8 (24 Kv) |  | 4999139.5 | 5863816.5 | 6954336 | 7030357 | 5578868 | 4475879 | 4310904 | 3964477.125 |  |  |  |  | 43177777.125 | 5397222.1406
Feeder # 9B (24Kv) |  | 4274225.25 | 2607787.671 | 0 | 0 | 1139488.6 | 1813588.4 | 1744764.5 | 1667335.5 |  |  |  |  | 13247189.921 | 2207864.9868
Feeder # 10A (24 Kv) |  | 0 | 832165 | 1843955 | 1859330 | 1776401 | 1880437 | 1763571 | 1653656 |  |  |  |  | 11609515 | 1658502.1429
Feeder # 10 (24 Kv) |  | 1532181 | 1548799.5 | 1485914.75 | 1507122.75 | 1467690.5 | 1404689.5 | 1280436.5 | 1221431.5 |  |  |  |  | 11448266 | 1431033.25
TOTALS |  | 24224639.68 | 24018220.301 | 22640152.75 | 22783668.5 | 21278928.85 | 20840383.15 | 19762575.81 | 18325243.315 |  |  |  |  | 173873812.356 | 21734226.5445
Feeder Planned Outages | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 2 (13 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 3 (13(Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 4 (13 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 5 (13 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 6 (13 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 6B (24 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feeder # 8 (24 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 9 (24Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 10 (24 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
TOTALS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder Forced Outages | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 1 | 2 | 4 | 1 | 0 | 0 | 2 | 1 |  |  |  |  | 11 | 1.8333
Feeder # 2 (13 Kv) |  | 9 | 2 | 7 | 4 | 4 | 1 | 3 | 3 |  |  |  |  | 33 | 4.125
Feeder # 3 (13(Kv) |  | 1 | 3 | 5 | 3 | 3 | 1 | 2 | 3 |  |  |  |  | 21 | 2.625
Feeder # 4 (13 Kv) |  | 1 | 3 | 5 | 2 | 2 | 1 | 2 | 3 |  |  |  |  | 19 | 2.375
Feeder # 5 (13 Kv) |  | 1 | 2 | 2 | 1 | 0 | 0 | 1 | 1 |  |  |  |  | 8 | 1.3333
Feeder # 6 (13 Kv) |  | 1 | 1 | 5 | 1 | 0 | 1 | 2 | 3 |  |  |  |  | 14 | 2
Feeder # 6B (24 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feeder # 8 (24 Kv) |  | 4 | 1 | 1 | 1 | 0 | 1 | 1 | 2 |  |  |  |  | 11 | 1.5714
Feeder # 9 (24Kv) |  | 2 | 1 | 0 | 0 | 0 | 2 | 2 | 2 |  |  |  |  | 9 | 1.8
Feeder # 10 (24 Kv) |  | 0 | 4 | 11 | 2 | 8 | 1 | 3 | 4 |  |  |  |  | 33 | 4.7143
TOTALS |  | 20 | 19 | 40 | 15 | 17 | 8 | 18 | 22 |  |  |  |  | 159 | 19.875
Feeder Total Outages HRS | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 0.41667 | 2.25 | 1.5833 | 1.9 | 0 | 0 | 4.5167 | 0.7 |  |  |  |  | 11.3667 | 1.8944
Feeder # 2 (13 Kv) |  | 1.75 | 15.9167 | 3.45 | 2.9833 | 1.3667 | 0.083333 | 5.8333 | 1.5333 |  |  |  |  | 32.9167 | 4.1146
Feeder # 3 (13(Kv) |  | 0.43333 | 4.35 | 2.85 | 0.53333 | 1.2167 | 0.033333 | 4.8 | 1.2667 |  |  |  |  | 15.4833 | 1.9354
Feeder # 4 (13 Kv) |  | 0.81667 | 3.0167 | 3.1833 | 2.3333 | 1.2167 | 0.083333 | 5.0667 | 1.8667 |  |  |  |  | 17.5833 | 2.1979
Feeder # 5 (13 Kv) |  | 0.41667 | 2.2333 | 0.81667 | 0.033333 | 0 | 0 | 0.4 | 0.7 |  |  |  |  | 4.6 | 0.76667
Feeder # 6 (13 Kv) |  | 0.83333 | 2.8167 | 3.05 | 1.9 | 0 | 0.1 | 5.5833 | 1.5667 |  |  |  |  | 15.85 | 2.2643
Feeder # 6B (24 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feeder # 8 (24 Kv) |  | 1.3833 | 2.2833 | 0.73333 | 0.033333 | 0 | 0.083333 | 0.5 | 1.0167 |  |  |  |  | 6.0333 | 0.8619
Feeder # 9 (24Kv) |  | 2.1 | 2.8333 | 0 | 0 | 0 | 0.2 | 5.7667 | 1.35 |  |  |  |  | 12.25 | 2.45
Feeder # 10 (24 Kv) |  | 0 | 6.5667 | 3.9167 | 2.1833 | 1.75 | 0.033333 | 5.8 | 1.5833 |  |  |  |  | 21.8333 | 3.119
Feeder loss sales KWH | [13 empty] | 0 | 0
Feeder # 1 (13Kv) |  | 762.3527 | 4122.2696 | 2651.819 | 3166.1563 | 0 | 0 | 6900.4953 | 1121.5803 |  |  |  |  | 18724.6733 | 3120.7789
Feeder # 2 (13 Kv) |  | 7643.2539 | 69018.1735 | 13881.2487 | 11510.9801 | 5087.7679 | 295.6336 | 20146.2502 | 5330.9474 |  |  |  |  | 132914.2553 | 16614.2819
Feeder # 3 (13(Kv) |  | 647.8577 | 6626.7147 | 4308.4537 | 779.3106 | 1640.3935 | 45.4282 | 6137.8896 | 1621.1904 |  |  |  |  | 21807.2384 | 2725.9048
Feeder # 4 (13 Kv) |  | 1694.8156 | 6344.4532 | 6594.0053 | 4717.4164 | 2356.3976 | 152.0134 | 8808.4525 | 3300.5961 |  |  |  |  | 33968.1501 | 4246.0188
Feeder # 5 (13 Kv) |  | 2179.7602 | 11200.2876 | 4122.0366 | 162.1936 | 0 | 0 | 1570.737 | 2815.4327 |  |  |  |  | 22050.4477 | 3675.0746
Feeder # 6 (13 Kv) |  | 2548.5277 | 8529.1968 | 8808.9292 | 5338.8464 | 0 | 266.2807 | 13866.4216 | 3898.6095 |  |  |  |  | 43256.8118 | 6179.5445
Feeder # 6B (24 Kv) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Feeder # 8 (24 Kv) |  | 9312.3096 | 18051.4316 | 7090.3416 | 314.9943 | 0 | 501.3867 | 2899.0612 | 6006.9327 |  |  |  |  | 44176.4577 | 6310.9225
Feeder # 9 (24Kv) |  | 12098.4944 | 9969.0556 | 0 | 0 | 0 | 487.6549 | 13629.1262 | 3356.3005 |  |  |  |  | 39540.6316 | 7908.1263
Feeder # 10 (24 Kv) |  | 0 | 13791.6875 | 8127.3121 | 4435.8013 | 3575.995 | 62.9369 | 10060.3247 | 2884.6735 |  |  |  |  | 42938.731 | 6134.1044
TOTALS |  | 36887.3718 | 147653.2701 | 55584.1463 | 30425.699 | 12660.5539 | 1811.3344 | 84018.7583 | 30336.2632 |  |  |  |  | 399377.3969 | 49922.1746
Plant Feeder Total Planned Outages | [13 empty] | 0 | 0
Feeder # 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 6B (24 Kv)
Feeder # 8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
TOTALS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Plant Feeder Total Forced Outages | [13 empty] | 0 | 0
Feeder # 1 |  | 0 | 2 | 4 | 0 | 0 | 0 | 2 | 0 |  |  |  |  | 8 | 2.6667
Feeder # 2 |  | 9 | 2 | 7 | 4 | 4 | 0 | 3 | 3 |  |  |  |  | 32 | 4.5714
Feeder # 3 |  | 0 | 3 | 5 | 3 | 3 | 0 | 2 | 3 |  |  |  |  | 19 | 3.1667
Feeder # 4 |  | 0 | 3 | 5 | 2 | 2 | 0 | 2 | 3 |  |  |  |  | 17 | 2.8333
Feeder # 5 |  | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 4 | 2
Feeder # 6 |  | 0 | 0 | 5 | 0 | 0 | 0 | 2 | 3 |  |  |  |  | 10 | 3.3333
Feeder # 6B (24 Kv)
Feeder # 8 |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  |  |  |  | 6 | 3
Feeder # 9 |  | 2 | 0 | 0 | 0 | 0 | 2 | 2 | 2 |  |  |  |  | 8 | 2
Feeder # 10 |  | 0 | 4 | 11 | 2 | 8 | 0 | 3 | 4 |  |  |  |  | 32 | 5.3333
TOTALS |  | 15 | 16 | 39 | 11 | 17 | 2 | 16 | 20 |  |  |  |  | 136 | 17
Plant Feeder Total Outages Time | [13 empty] | 0 | 0
Feeder # 1 |  | 0.41667 | 2.25 | 1.5833 | 1.9 | 0 | 0 | 4.5167 | 0.7 |  |  |  |  | 11.3667 | 1.8944
Feeder # 2 |  | 1.75 | 15.9167 | 3.45 | 2.9833 | 1.3667 | 0.083333 | 5.8333 | 1.5333 |  |  |  |  | 32.9167 | 4.1146
Feeder # 3 |  | 0.43333 | 4.35 | 2.85 | 0.53333 | 1.2167 | 0.033333 | 4.8 | 1.2667 |  |  |  |  | 15.4833 | 1.9354
Feeder # 4 |  | 0.81667 | 3.0167 | 3.1833 | 2.3333 | 1.2167 | 0.083333 | 5.0667 | 1.8667 |  |  |  |  | 17.5833 | 2.1979
Feeder # 5 |  | 0.41667 | 2.2333 | 0.81667 | 0.033333 | 0 | 0 | 0.4 | 0.7 |  |  |  |  | 4.6 | 0.76667
Feeder # 6 |  | 0.83333 | 2.8167 | 3.05 | 1.9 | 0 | 0.1 | 5.5833 | 1.5667 |  |  |  |  | 15.85 | 2.2643
Feeder # 6B (24 Kv)
Feeder # 8 |  | 1.3833 | 2.2833 | 0.73333 | 0.033333 | 0 | 0.083333 | 0.5 | 1.0167 |  |  |  |  | 6.0333 | 0.8619
Feeder # 9 |  | 2.1 | 2.8333 | 0 | 0 | 0 | 0.2 | 5.7667 | 1.35 |  |  |  |  | 12.25 | 2.45
Feeder # 10 |  | 0 | 6.5667 | 3.9167 | 2.1833 | 1.75 | 0.033333 | 5.8 | 1.5833 |  |  |  |  | 21.8333 | 3.119
TOTALS | [13 empty] | 0 | 0
Plant Feeder Total Loss sales | [13 empty] | 0 | 0
Feeder # 1 |  | 762.3527 | 4122.2696 | 2651.819 | 3166.1563 | 0 | 0 | 6900.4953 | 1121.5803 |  |  |  |  | 18724.6733 | 3120.7789
Feeder # 2 |  | 7643.2539 | 69018.1735 | 13881.2487 | 11510.9801 | 5087.7679 | 295.6336 | 20146.2502 | 5330.9474 |  |  |  |  | 132914.2553 | 16614.2819
Feeder # 3 |  | 647.8577 | 6626.7147 | 4308.4537 | 779.3106 | 1640.3935 | 45.4282 | 6137.8896 | 1621.1904 |  |  |  |  | 21807.2384 | 2725.9048
Feeder # 4 |  | 1694.8156 | 6344.4532 | 6594.0053 | 4717.4164 | 2356.3976 | 152.0134 | 8808.4525 | 3300.5961 |  |  |  |  | 33968.1501 | 4246.0188
Feeder # 5 |  | 2179.7602 | 11200.2876 | 4122.0366 | 162.1936 | 0 | 0 | 1570.737 | 2815.4327 |  |  |  |  | 22050.4477 | 3675.0746
Feeder # 6 |  | 2548.5277 | 8529.1968 | 8808.9292 | 5338.8464 | 0 | 266.2807 | 13866.4216 | 3898.6095 |  |  |  |  | 43256.8118 | 6179.5445
Feeder # 6B (24 Kv)
Feeder # 8 |  | 9312.3096 | 18051.4316 | 7090.3416 | 314.9943 | 0 | 501.3867 | 2899.0612 | 6006.9327 |  |  |  |  | 44176.4577 | 6310.9225
Feeder # 9 |  | 12098.4944 | 9969.0556 | 0 | 0 | 0 | 487.6549 | 13629.1262 | 3356.3005 |  |  |  |  | 39540.6316 | 7908.1263
Feeder # 10 |  | 0 | 13791.6875 | 8127.3121 | 4435.8013 | 3575.995 | 62.9369 | 10060.3247 | 2884.6735 |  |  |  |  | 42938.731 | 6134.1044
TOTALS |  | 36887.3718 | 147653.2701 | 55584.1463 | 30425.699 | 12660.5539 | 1811.3344 | 84018.7583 | 30336.2632 |  |  |  |  | 399377.3969 | 49922.1746
Line Feeder Total Planned Outages | [13 empty] | 0 | 0
Feeder # 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 6B (24 Kv)
Feeder # 8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
TOTALS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Line Feeder Total Forced Outages | [13 empty] | 0 | 0
Feeder # 1 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 |  |  |  |  | 3 | 1
Feeder # 2 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  |  |  |  | 1 | 1
Feeder # 3 |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  |  |  |  | 2 | 1
Feeder # 4 |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  |  |  |  | 2 | 1
Feeder # 5 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 |  |  |  |  | 4 | 1
Feeder # 6 |  | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 0 |  |  |  |  | 4 | 1
Feeder # 6B (24 Kv)
Feeder # 8 |  | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 0 |  |  |  |  | 5 | 1
Feeder # 9 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1 | 1
Feeder # 10 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  |  |  |  | 1 | 1
TOTALS |  | 5 | 3 | 1 | 4 | 0 | 6 | 2 | 2 |  |  |  |  | 23 | 3.2857
Line Feeder Total Outages Time | [13 empty] | 0 | 0
Feeder # 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 6B (24 Kv)
Feeder # 8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
TOTALS | [13 empty] | 0 | 0
Line Feeder Total Loss sales | [13 empty] | 0 | 0
Feeder # 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 6B (24 Kv)
Feeder # 8 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Feeder # 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
TOTALS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
pag6 | [13 empty] | 0 | 0
Units Outages | [13 empty] | 0 | 0
Unit 10 ST | [13 empty] | 8 | 1 | bar: 7 to 14
Unit 11 ST | [13 empty] | 8 | 1 | bar: 7 to 14
Unit 11 BLR | [13 empty] | 8 | 1 | bar: 7 to 14
Unit 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 17 |  | 1 | 1 | 2 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 4 | 1.3333
Unit 19 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 20 | [13 empty] | 8 | 1 | bar: 7 to 14
Aggreko |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
HRSG 21 | [13 empty] | 8 | 1 | bar: 7 to 14
HRSG 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Units Outages Duration | [13 empty] | 0 | 0
Unit 10 ST |  | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 |  |  |  |  | 5832 | 729
Unit 11 ST |  | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 |  |  |  |  | 5832 | 729
Unit 11 BLR |  | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 |  |  |  |  | 5832 | 729
Unit 16 |  | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 |  |  |  |  | 5832 | 729
Unit 17 |  | 0 | 0 | 26.65 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 26.65 | 26.65
Unit 19 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 20 |  | 744 | 744 | 720 | 744 | 720 | 723.3167 | 0 | 0 |  |  |  |  | 4395.3167 | 732.5528
Aggreko |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
HRSG 21 |  | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 |  |  |  |  | 5832 | 729
HRSG 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit Planned Outages | [13 empty] | 0 | 0
Unit 10 ST | [13 empty] | 8 | 1 | bar: 7 to 14
Unit 11 ST | [13 empty] | 8 | 1 | bar: 7 to 14
Unit 11 BLR | [13 empty] | 8 | 1 | bar: 7 to 14
Unit 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 17 |  | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2 | 1
Unit 19 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 20 | [13 empty] | 8 | 1 | bar: 7 to 14
Aggreko |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
HRSG 21 | [13 empty] | 8 | 1 | bar: 7 to 14
HRSG 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Unit Planned Outages Duration | [13 empty] | 0 | 0
Unit 10 ST |  | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 |  |  |  |  | 5832 | 729
Unit 11 ST |  | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 |  |  |  |  | 5832 | 729
Unit 11 BLR |  | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 |  |  |  |  | 5832 | 729
Unit 16 |  | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 |  |  |  |  | 5832 | 729
Unit 17 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 19 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 20 |  | 744 | 744 | 720 | 744 | 720 | 723.3167 | 0 | 0 |  |  |  |  | 4395.3167 | 732.5528
Aggreko |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
HRSG 21 |  | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 |  |  |  |  | 5832 | 729
HRSG 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Unit Forced Outages |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 10 ST |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 11 ST |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 11 BLR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 17 |  | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2 | 2
Unit 19 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 20 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Aggreko |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
HRSG 21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
HRSG 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Unit Forced Outages Duration |  | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2 | 2
Unit 10 ST |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 11 ST |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 11 BLR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 17 |  | 0 | 0 | 26.65 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 26.65 | 26.65
Unit 19 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 20 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Aggreko |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 4 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
IDE 9 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
HRSG 21 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
HRSG 24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Plant Power Distribution | [13 empty] | 0 | 0
Total 13KV Feeders |  | 13419093.93 | 13165651.63 | 12355947 | 12386858.75 | 11316480.75 | 11265789.25 | 10662899.81 | 9818343.19 |  |  |  |  | 94391064.31 | 11798883.0388
Total 24KV Feeders |  | 10805545.75 | 10852568.671 | 10284205.75 | 10396809.75 | 9962448.1 | 9574593.9 | 9099676 | 8506900.125 |  |  |  |  | 79482748.046 | 9935343.5058
Feeder Totals |  | 24224639.68 | 24018220.301 | 22640152.75 | 22783668.5 | 21278928.85 | 20840383.15 | 19762575.81 | 18325243.315 |  |  |  |  | 173873812.356 | 21734226.5445
Total Generation |  | 25719989.5 | 25797063.5 | 24243512.5 | 24404586 | 22938640 | 22207306.406 | 21720886.844 | 19883892.25 |  |  |  |  | 186915877 | 23364484.625
24 KV BUS at XFMR-1 (T1) |  | 66909.75 | 391221.84 | 1276007.57 | 55735.12 | 63357.25 | 36349 | 26179.75 | 144837 |  |  |  |  | 2060597.28 | 257574.66
24 KV BUS at XFMR-2 (T2) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
24 KV BUS at XFMR-3 (T3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
XFMR T1 in |  | 66510 | 389244 | 1270567 | 55447 | 62657 | 36161 | 25980 | 144012
XFMR T1 out |  | 4351087 | 4122766 | 4142281 | 5145701 | 4707082 | 5536054 | 7918545 | 4548740
XFMR T3 in |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XFMR T3 out |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XFMR T4in (from #16) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XFMR T4 out ( |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
XFMR T5 in (from #20) |  | 0 | 99999416 | 584 | 0 | 0 | 81566 | 2583105 | 0
XFMR T5 out |  | 5558411 | 5172388 | 4438906 | 4536047 | 4221366 | 3120464 | 1798985 | 3598643
T1 &T3&T4 & T5 Available |  | 9976008 | 109683814 | 9852338 | 9737195 | 8991105 | 8774245 | 12326615 | 8291395 |  |  |  |  | 177632715 | 22204089.375
T1 &T3 & T4 & T5 Losses |  | 47669.07 | 366338.699 | 251331.5 | 237737.5 | 312477.1 | 41634.314 | 368462.654 | 117165.435 |  |  |  |  | 1742816.272 | 217852.034
Net Distributed |  | 25672320.43 | 25430724.801 | 23992181 | 24166848.5 | 22626162.9 | 22165672.092 | 21352424.19 | 19766726.815 |  |  |  |  | 185173060.728 | 23146632.591
Line Department |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Water Department |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Power Plant Services |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Administration & General |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Plant Station Service |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Net Available from Bus |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Wapa KWH From Dist |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
SwitchGear Bkr1 SS |  | 1126712.5 | 1097708.5 | 1046123 | 1076282.5 | 1059253 | 1087062.87 | 1218442.13 | 1079256.5 |  |  |  |  | 8790841 | 1098855.125
SwitchGear Bkr3 SS |  | 301288.25 | 306636 | 302425.25 | 302817.5 | 284381.05 | 317414.7 | 369246.25 | 361867 |  |  |  |  | 2546076 | 318259.5
Total Station Service Power |  | 1437840.75 | 1408424.5 | 1350288.25 | 1381140 | 1345434.05 | 1406517.57 | 1588768.38 | 1441303.5 |  |  |  |  | 11359717 | 1419964.625
Net KWH Available for Sale |  | 24234479.68 | 24022300.301 | 22641892.75 | 22785708.5 | 21280728.85 | 20759154.522 | 19763655.81 | 18325423.315 |  |  |  |  | 173813343.728 | 21726667.966
Plant Unaccountable |  | 0 | 0 | 0 | 0 | 0 | -83268.628 | 0 | 0
Peak Load: |  | 41080 | 41790 | 40070 | 39340 | 39400 | 37330 | 38220 | 35500 |  |  |  |  | 312730 | 39091.25
Day |  | Thursday | Sunday | Tuesday | Saturday | Sunday | Friday | Saturday | Wednesday | [5 empty] | 0
Date |  | 2020-07-02 | 2020-08-16 | 2020-09-29 | 2020-10-10 | 2020-11-08 | 2021-12-17 | 2021-01-16 | 2021-02-03
Hour |  | 19:20 | 19:21 | 19:00 | 18:39 | 19:00 | 18:00 | 20:00 | 0.78264
Min Load |  | 27650 | 26320 | 25710 | 25910 | 24450 | 23490 | 23290 | 23290 |  |  |  |  | 200110 | 25013.75
Day |  | Sunday | Wednesday | Sunday | Thursday | Sunday | Tuesday | Thursday | Sunday
Date |  | 2020-07-19 | 2020-08-05 | 2020-09-20 | 2020-10-29 | 2020-11-29 | 2021-12-07 | 2021-01-07 | 44234
Hour |  | 6:00 | 6:00 | 4:00 | 3:00 | 7:00 | 4:00 | 4:00 | 0.20833 | [5 empty] | 4:52
Pag 7
No 6 Fuel For Power |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
No 6 Fuel For Water |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
No 2 Fuel For Power |  | 5520.1249 | 9234.3241 | 16758.6572 | 1935.0103 | 2188.4473 | 2056.614 | 4149.3782 | 1607.2953 |  |  |  |  | 43449.8514 | 5431.2314
No 2 Fuel For Water |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
O&M Factor for Water |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
BLR11FUEL2COST |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Firing | [13 empty] | 0 | 0
WHBSFCAE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Power Boilers | [13 empty] | 0 | 0
[14 empty] | 0 | 0
TPBSFC | [13 empty] | 0 | 0
BLR11FUELCOST |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Combined Cycle | [13 empty] | 0 | 0
WHB, 16 & 17 | [13 empty] | 0 | 0
TGTFC | [13 empty] | 0 | 0
GEN161720FUELCOST |  | 1999545.5291 | 1924719.682 | 1614411.4254 | 1804814.6582 | 1759979.7993 | 1914831.8574 | 2474540.2423 | 1996028.5493 |  |  |  |  | 15488871.743 | 1936108.9679
Simple Cycle | [13 empty] | 0 | 0
12 & 14 & 22 | [13 empty] | 0 | 0
GEN 19FUELCOST |  | 343756.9591 | 495210.025 | 787472.5538 | 88884.4036 | 129727.8244 | 63153.6403 | 182272.3202 | 63584.2339 |  |  |  |  | 2154061.9602 | 269257.745
DIESEL | [13 empty] | 0 | 0
7 St. John | [13 empty] | 0 | 0
DIESEL_EMER. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
GT Fuel Allocation | [13 empty] | 0 | 0
HP Stm from WHB | [13 empty] | 0 | 0
GTFCAE | [13 empty] | 0 | 0
WHBHPSTMCOST |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
whb Benefit | [13 empty] | 0 | 0
Equalization to Water | [13 empty] | 0 | 0
WHBBECW | [13 empty] | 0 | 0
WHBBENCOSTWTR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Extraction Benefit | [13 empty] | 0 | 0
Equalization to Water | [13 empty] | 0 | 0
BECW | [13 empty] | 0 | 0
BENEQFCOSTWTR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Gas Turbine | [13 empty] | 0 | 0
Power Allocation | [13 empty] | 0 | 0
GTFCA | [13 empty] | 0 | 0
GEN161720ADJFCOST |  | 1999545.5291 | 1924719.682 | 1614411.4254 | 1804814.6582 | 1759979.7993 | 1914831.8574 | 2474540.2423 | 1996028.5493 |  |  |  |  | 15488871.743 | 1936108.9679
Extraction Incremental | [13 empty] | 0 | 0
to Water | [13 empty] | 0 | 0
FCAWI | [13 empty] | 0 | 0
INCRFUELCOSTWTR |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
GT Fuel Allocation | [13 empty] | 0 | 0
LP Stm from WHB | [13 empty] | 0 | 0
WHBFCAW | [13 empty] | 0 | 0
WHBLPSTMCOST |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Electrc Power | [13 empty] | 0 | 0
Generation | [13 empty] | 0 | 0
TOTFUELCOSTPWR |  | 3713314.5045 | 3744752.5614 | 3562453.9143 | 3315497.8093 | 3275251.6783 | 3496583.1529 | 4188975.5048 | 3662267.9831 |  |  |  |  | 28959097.1085 | 3619887.1386
RO Electricity cost |  | 70963.9268 | 74207.1698 | 62238.2739 | 65426.4231 | 65607.1959 | 78153.5202 | 108141.6507 | 85982.2109 |  |  |  |  | 610720.3713 | 76340.0464
UPW Electicity Cost |  | 2771.5908 | 2670.0228 | 2442.0318 | 2235.9573 | 2189.1774 | 2524.0904 | 3269.6675 | 2751.7675 |  |  |  |  | 20854.3055 | 2606.7882
RO Annex Electricity cost |  | 96033.7397 | 88297.0049 | 89701.1334 | 84224.1728 | 89743.4627 | 98096.1286 | 137721.6401 | 122647.8916
TOTFUELCSRWTR |  | 166997.6665 | 162504.1747 | 151939.4073 | 149650.5959 | 155350.6585 | 176249.6488 | 245863.2908 | 208630.1026 |  |  |  |  | 1417185.5451 | 177148.1931
Pag8 | [13 empty] | 0 | 0
No 2 BBLS | [13 empty] | 0 | 0
Inventory-Beginning of Month |  | 39740.5629 | 34220.4379 | 57168.2338 | 40409.5766 | 38474.5663 | 36286.119 | 34229.505 | 30080.1268 |  |  |  |  | 310609.1282 | 38826.141
Received During Month |  | 0 | 32182.12 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 32182.12 | 32182.12
Consumed During Month |  | 5520.1249 | 9234.3241 | 16758.6572 | 1935.0103 | 2188.4473 | 2056.614 | 4149.3782 | 1607.2953 |  |  |  |  | 43449.8514 | 5431.2314
Inventory-End of Month |  | 34220.4379 | 57168.2338 | 40409.5766 | 38474.5663 | 36286.119 | 34229.505 | 30080.1268 | 28472.8314 |  |  |  |  | 299341.3967 | 37417.6746
Calorific Value (BTU/GAL) |  | 136784.2908 | 136999.0879 | 136999.0879 | 136999.0879 | 136999.0879 | 136999.0879 | 136999.0879 | 136999.0879 |  |  |  |  | 1095777.9063 | 136972.2383
Calorific Value (BTU/GAL) |  | 136784.2908 | 136999.0879 | 136999.0879 | 136999.0879 | 136999.0879 | 136999.0879 | 136999.0879 | 136999.0879 |  |  |  |  | 1095777.9063 | 136972.2383
No 6 BBLS | [13 empty] | 0 | 0
Inventory-Beginning of Month |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Received During Month |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Consumed During Month |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Inventory-End of Month |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Calorific Value (BTU/GAL) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
PROPANE
Propane Value (BTU/Gal) |  | 91735 | 91735 | 91735 | 91647 | 91647 | 91425 | 91425 | 91425
End of Month- Fuel in Tanks | [13 empty] | 0 | 0
No 2 BBLS | [13 empty] | 0 | 0
Tank 1 #2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Tank 2 #2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Tank 5 #2 |  | 8440.91 | 37021.4 | 30852.38 | 28860.59 | 26657.03 | 24785.45 | 20278.4 | 18987.72 |  |  |  |  | 195883.88 | 24485.485
Tank 6 #2 |  | 17422.64 | 11760.45 | 1141.19 | 1124.68 | 1127.88 | 944.64 | 1240.9 | 944.64 |  |  |  |  | 35707.02 | 4463.3775
TOTAL |  | 34220.44 | 57168.23 | 40409.58 | 38474.57 | 36286.12 | 34229.5 | 30080.13 | 28472.83 |  |  |  |  | 299341.4 | 37417.675
No 6 BBLS | [13 empty] | 0 | 0
Tank 3 #2 |  | 4452.57 | 4450.29 | 4453.2 | 4451.44 | 4450.51 | 4444.46 | 4450.11 | 4425.75 |  |  |  |  | 35578.33 | 4447.2913
Tank 4 #6 |  | 3904.33 | 3936.1 | 3962.8 | 4037.85 | 4050.7 | 4054.95 | 4110.72 | 4114.71 |  |  |  |  | 32172.16 | 4021.52
Tank 7 #6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
TOTAL |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
[14 empty] | 0 | 0
Fuel Shipments | [13 empty] | 0 | 0
Date(1) |  | 0 | 2020-08-19 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2020-08-19 | 2020-08-19
No2 BBLS |  | 0 | 32182.12 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 32182.12 | 32182.12
Date(2) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
No2 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Date(3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
No2 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Date(4) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
No2 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Date(5) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
No2 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Date(6) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
No2 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Date(7) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
No2 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Date(8) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
No2 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Date(9) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
No2 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
TOTAL SHIPMENTS No 2 |  | 0 | 32182.12 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 32182.12 | 32182.12
Date(1) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
No6 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Date(2) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
No6 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Date(3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
No6 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Date(4) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
No6 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Date(5) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
No6 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Date(6) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
No6 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Date(7) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
No6 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Date(8) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
No6 BBLS |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
TOTAL SHIPMENTS No 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
[14 empty] | 0 | 0
Fuel Allocations Amount | [13 empty] | 0 | 0
Electric Power Generation |  | 3713314.5045 | 3744752.5614 | 3562453.9143 | 3315497.8093 | 3275251.6783 | 3496583.1529 | 4188975.5048 | 3662267.9831 |  |  |  |  | 28959097.1085 | 3619887.1386
Water Production |  | 166997.6665 | 162504.1747 | 151939.4073 | 149650.5959 | 155350.6585 | 176249.6488 | 245863.2908 | 208630.1026 |  |  |  |  | 1417185.5451 | 177148.1931
Total #2 Fuel Cost |  | 426605.2954 | 639765.748 | 1161061.1421 | 134059.983 | 151618.4179 | 142478.9617 | 287462.368 | 111350.8443 |  |  |  |  | 3054402.7603 | 381800.345
BBLS No. 6 for Power |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
BBLS No.6 for Water |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
BBLS No. 2 for Power |  | 5520.1249 | 9234.3241 | 16758.6572 | 1935.0103 | 2188.4473 | 2056.614 | 4149.3782 | 1607.2953 |  |  |  |  | 43449.8514 | 5431.2314
BBLS No.2 for Water |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
No. 6 BBL Cost |  | 71.9034 | 71.9034 | 71.9034 | 71.9034 | 71.9034 | 71.9034 | 71.9034 | 71.9034 |  |  |  |  | 575.2271 | 71.9034
No. 2 BBL Cost |  | 77.2818 | 69.2813 | 69.2813 | 69.2813 | 69.2813 | 69.2784 | 69.2784 | 69.2784 |  |  |  |  | 562.2422 | 70.2803
Propane Cost per Bbl |  | 38.3544 | 38.262 | 37.5354 | 38.1612 | 39.7362 | 43.26 | 52.8234 | 52.1514
Propane Consumed
Unit 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
Unit 17 |  | 2098879.9746 | 1954076.7936 | 1388410.9176 | 1936648.7771 | 1837109.4026 | 1757927.9258 | 926509.918 | 152377.8603 |  |  |  |  | 12051941.5695
Unit 20 |  | 0 | 0 | 0 | 0 | 0 | 24117.2548 | 957365.5646 | 1416650.0361 |  |  |  |  | 2398132.8555 | 799377.6185
Aggreko |  | 1683103.0254 | 1632631.2064 | 1468624.0824 | 1729528.2229 | 1628680.5974 | 1645482.8194 | 1413712.5174 | 1458714.1036 |  |  |  |  | 12660476.575
No. 2 Units BBLS No. 2 Consumed | [13 empty] | 0 | 0
Unit 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 11 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 16 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Unit 17 |  | 1072.0288 | 2086.5049 | 5392.3457 | 652.0604 | 315.967 | 443.7555 | 873.1619 | 337.2299 |  |  |  |  | 11173.0543 | 1396.6318
Unit 19 |  | 4448.0961 | 7147.8192 | 11366.3115 | 1282.9499 | 1872.4803 | 911.5919 | 2631.0115 | 917.8075 |  |  |  |  | 30578.0679 | 3822.2585
Unit 20 |  | 0 | 0 | 0 | 0 | 0 | 701.2667 | 645.2048 | 352.2579 |  |  |  |  | 1698.7293 | 566.2431
Diesel Emergency |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0
Total No. 2 Consumed |  | 5520.1249 | 9234.3241 | 16758.6572 | 1935.0103 | 2188.4473 | 2056.614 | 4149.3782 | 1607.2953 |  |  |  |  | 43449.8514 | 5431.2314
Note on I673: Nicholson: negative

## PR-Pag1
February - 2021
Production Summary |  |  |  |  | Generating Units Heat Rate |  | FYTD | This Month
|  | FYTD | FYTD |  | (Gross Energy in KWH Produced) | This Month | AVG. | %
Item | This Month | AVG. | TOTAL | Units | Units | BTU/KWH | BTU/KWH | Efficiency
Total System Gross Generation** | 19883.8923 | 23364.4846 | 186915.877 | MWH
Gross Power Plant Generation | 19245.18 | 22733.0863 | 181864.69 | MWH
Gross Water Production | 87791.8333 | 89140.6458 | 713125.1667 | KGAL
System Load Factor | 80.67% | 79.66% |  | % | Unit 10-Steam (10 MW) + WHBs* | N/A | N/A | N/A
Total Propane Fuel Cost | 3759547.2414 | 3415234.9867 | 27321879.8933 | $ | Unit 11-Steam (19.1 MW) + WHBs | N/A | N/A | N/A
Total No. 2 Fuel Cost | 111350.8443 | 381800.345 | 3054402.7603 | $ | Unit 16-Gas Turbine (22.5 MW) | 0 | 0 | 0%
Power Fuel Cost (Internal) | 0.20114 | 0.16852 |  | $/KWH | Unit 17-Gas Turbine (21.9 MW) | 18459.59 | 20189.82 | 18.48%
Power Fuel Cost (to bus) | 0.21123 | 0.17651 |  | $/KWH | Unit 19-Gas Turbine (24.5 MW) | 18210.45 | 23150.92 | 18.74%
Water Fuel Cost (Internal) | 2.3764 | 1.9794 |  | $/KGAL | Unit 20_Gas Turbine (24.5 MW) | 21478.41 | 27847.89 | 15.89%
Water Fuel Cost (to Distribution) | 2.4197 | 2.0149 |  | $/KGAL | Aggreko (20.0 MW) | 11140.59 | 10968.1 | 30.63%
Total Power Fuel Cost | 3662267.9831 | 3619887.1386 | 28959097.1085 | $ | Total Electric Generation Only | 14863.96 | 15027.1 | 22.96%
Total Water Cost | 208630.1026 | 177148.1931 | 1417185.5451 | $ | *Note:Total Electric Generation includes values of steam provided to STG #10 and #11 by HRSGs
Propane consumed | 72089.0952 | 80686.1637 | 645489.3095 | BBLS
No. 2 Fuel Consumed | 1607.2953 | 5431.2314 | 43449.8514 | BBLS
[5 empty] | Power Units Availability |  | FYTD
No. 2 Fuel Received | 0 | 32182.12 | 32182.12 | BBLS |  | This Month | AVG.
[5 empty] | Unit | Percent (%) | Percent (%)
EOM No. 2 Fuel On Hand* | 14.2364 | 18.7088 |  | DAYS
Plant Water Use ( Internal | 1406.5682 | 3459.7486 | 27677.9888 | $ | Unit 10 | 0% | 0%
Plant Power Use (Internal) | 277296.7445 | 223292.2121 | 1786337.6971 | $ | Unit 11 | 0% | 0%
7SEAS RO 1 Electricity Cost | 85982.2109 |  |  | $ | Unit 16 | 0% | 0%
7SEAS UPW Electricity Cost | 2751.7675 |  |  | $ | Unit 17 | 100% | 99.54%
7SEAS RO 2 Electricity Cost | 122647.8916 |  |  | $ | Unit 19 | 100% | 100%
**Note: Includes power generated by solar |  |  |  |  | Unit 20 | 100% | 25.35%
*Note: Based on 2000Bbl/day consumption |  |  |  |  | Aggreko | 100% | 100%
[5 empty] | HRSG 21 | 0% | 0%
[5 empty] | HRSG 24 | 100% | 100%

## PR-Pag2
February - 2021
Power Generation - Station Power |  | FYTD | TOTAL | Generating Units Average Loading |  |  | FYTD | Utilization
Item | This Month | Monthly | FYTD |  |  | This Month | AVG. | Factor
| KWH | AVG. | KWH | (KWH / Operating Hours) |  | KW | KW | Percent
Steam Turbine Generation | 0 | 0 | 0 | Unit 10 |  | 0 | 0 | 0%
Gas Turbine Generation | 19245180 | 22733086.25 | 181864690 | Unit 11 |  | 0 | 0 | 0%
Diesel Generation | 0 | 0 | 0 | Unit 16 |  | 0 | 0 | 0%
Total Generation | 19245180 | 22733086.25 | 181864690 | Unit 17 |  | 10720.6983 | 11928.6894 | 48.95%
Steam Station Power | 0 | 0 | 0 | Unit 19 |  | 10000 | 8057.5766 | 40.82%
Gas Turbine Station Power | 115400 | 61802.5 | 494420 | Unit 20 |  | 10331.444 | 9682.3073 | 42.17%
Aggreko Station Service | 790 | 702.5 | 5620 | Aggreko |  | 19704.4402 | 19525.8307 | 98.52%
Total Gen. Plant Station Power | 115400 | 61802.5 | 494420 | Diesel |  | 0 | 0 | 0%
Total Service / Gross Output | 0.5996% | 0.2833%
IPP1 | 638712.25 | 631398.375 | 5051187
Total System Generation | 19883892.25 | 22733086.25 | 181864690
Generating Units Station Power
Generating Units Operating Hours |  | FYTD | TOTAL |  |  | FYTD | TOTAL | This Month | FYTD | FYTD
| This Month | Monthly | FYTD |  | This Month | AVG. | FYTD | SS Power | AVG. | SS Power
Unit | HRS | AVG. | HRS | Unit | KWH | KWH | KWH | KWH | KWH | KWH
Unit 10 | 0 | 0 | 0 | Unit 10 | 0 | 0 | 0 | 0 | 0 | 0
Unit 11 | 0 | 0 | 0 | Unit 11 | 0 | 0 | 0 | 0 | 0 | 0
Unit 16 | 0 | 0 | 0 | Unit 16 | 0 | 0 | 0 | 0 | 0 | 0
Unit 17 | 80.2 | 590.875 | 4727 | Unit 17 | 859800 | 7192720 | 57541760 | 23790 | 7227.5 | 57820
Unit 19 | 29 | 119.4625 | 955.7 | Unit 19 | 290000 | 978750 | 7830000 | 22800 | 30060 | 240480
Unit 20 | 592.8 | 337.9 | 1013.7 | Unit 20 | 6124480 | 3568160 | 10704480 | 68810 | 24515 | 196120
Aggreko | 607.523 | 688.3744 | 4818.6205 | Aggreko | 11970900 | 13223556.25 | 105788450 | 790 | 702.5 | 5620
Diesel Generation(Emergency) | 2 | 1.7143 | 12 | Diesel | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | TOTAL | 19245180 | 22733086.25 | 181864690 | 116190 | 62010 | 496080

## PR-Pag3
February - 2021
BOILERS/STM. TURBINES | SS | GAS TURBINE | SS | STX. EMERGENCY DIESEL | SS | OTHERS | SS
| Kwh |  | Kwh |  | Kwh |  | Kwh
SS10 Plant Aux. Trans 480V | 0 | Plant SS |  | Diesel | 0 | Station Service Shops | 26640
SS10 Unit Aux.. Trans 480V | 0 | Unit 16 | 0 |  |  | Station Service Office | 0
|  | Unit 17 | 23610 |  |  | Fuel Tanks SS | 0
Unit 10 Total Station Power | 0 | Unit 19 | 22800 | TOTAL DIESEL | 0 | Switch Yard SS | 166240
|  | Unit 20 | 68810 |  |  | Richmond Sub SS | 591
|  | Aggreko | 790 |  |  | Midland Sub SS | 18052
SS11 Plant Aux. Trans 480V | 0 |  |  |  |  | TOTAL OTHERS | 211523
SS11 Unit Aux.. Trans 480V | 0 | Unit SS |  | WATER PLANTS | SS
|  | Unit 16 | 0 |  | Kwh | SwitchGear Bkr1 SS | 1079256.5
Unit 11 Net Total Station Power | 0 | Unit 17 | 180 | Plant ABC Pump usage | 0 | SwitchGear Bkr3 SS | 361867
|  | Unit 19 | 0 |  |  | SS10 Unit Aux Trans. | 0
|  | Unit 20 | 0 | Intake Pump A&B+Chloropac | 0 | SS11 Unit Aux Trans. | 0
HRSG 21 Station Power | 0 | TOTAL GAS TURBINES | 116190 |  |  | Total GT Unit SS | 180
HRSG 24 Station Power** | 0 | Plant Pumps |  | RO Plant Electrical Usage | 427483
|  | Intake Pump A | 0 | UPW Electrical Usage | 13681.13 |  | 1441303.5
|  | Intake Pump B | 0 | RO ANNEX Electrical Usage | 609776
WHB Net Station Power | 0 | Intake Pump C | 0
TOTAL BOILERS / STM TURBINES | 0 |  |  | TOTAL WATER PLANTS | 1050940.13 | Total Station Service* | 1378653.13
*Total SS switched to a summaton of individual meters from general 'main' distribution meters summation
** No power to meter

## PR-Pag4
February - 2021
Desalination Plants Summary
|  | FYTD | TOTAL | Units Water Output
| Service | AVG. | FYTD | This Month | FYTD
Unit | HRS | HRS | HRS | GALS | GALS
RO 1 |  |  |  | 35765500 | 300102500
RO 2 |  |  |  | 52026333.3333 | 413022666.6667
STX TOTALS |  |  |  | 87791833.3333 | 713125166.6667
Boilers Summary
|  | Boilers Service Hours |  |  | Make Up Feed Water |  | Low Pressure Steam |  | High Pressure Steam
| Service | AVG. | FYTD | This Month | AVG. | FYTD | This Month | FYTD | This Month | FYTD
Unit | HRS | HRS | HRS | GALS | GALS | GALS | LBS | AVG. | LBS | AVG.
HRSG 21/IPOS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HRSG 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Boiler 11 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
TOTALS |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Distribution |  | This Month | FYTD-AVG. | FYTD |  | Steam Summary |  | LP Steam | HP Steam
|  | GALS | GALS | GALS |  | ITEM |  | LBS | LBS
Total Plant Water Produced |  | 87791833.3333 | 89140645.8333 | 713125166.6667 |  | Total Steam Produced |  | 0 | 0
Total Reverse Osmosis Produced |  | 87791833.3333 | 37512812.5 | 300102500 |  | To Steam Turbine 10 |  |  | 0
Total to Distribution Tank |  | 86222022.3333 | 87574296.25 | 700594370 |  | To Steam Turbine 11 |  |  | 0
Apparent Station Use |  | 1569811 | 1566349.5833 | 12530796.6667 |  | From Steam Turbine 10 |  | 0 | 0
Water to day Tank |  | 889333.3333 | 1075208.3333 | 8601666.6667 |  | From Steam Turbine 11 |  | 0
UPW Feed |  | 1535311 | 1536637.0833 | 12293096.6667
UPW Product |  | 889333.3333 | 1075208.3333 | 8601666.6667 |  | Used Steam for Production |  | 0 | 0
Water to the Demineralizer (Regen) |  | 0 | 0 | 0 |  | Others uses & Deareator |  |  | 0
Boilers Make Up |  | 0 | 0 | 0
Unit 16 Noxwater |  | 0 | 0 | 0
Unit 17 Noxwater |  | 51999.1455 | 1574028.717 | 12592229.7363
Unit 19 Noxwater |  | 25788.1718 | 118567.3935 | 948539.1483
Unit 20 Noxwater |  | 479598.5107 | 280336.3851 | 841009.1553
Metered Total Wtr to NOX |  | 796200 | 945162.5 | 7561300
Station Wtr Warehouse & Eng. |  | 0 | 0 | 0
Plant Service Water |  | 34500 | 29712.5 | 237700
Admin. Off. Water |  | 0 | 0 | 0
WTR to Fire Hydrants |  | 0 | 0 | 0 |  | * Unaccountable value has been zeroed due to non-functional distribution
Total Water used |  | 1569811 | 1566349.5833 | 12530796.6667 |  |  | meter giving rise to high unaccountable value
Unaccountable Water |  | 0 | 0 | 0

## PR-Pag5
February - 2021
| Feeders Power Distribution |  | This Month Total Plant Outages |  |  | Month | FYTD | FYTD | Feeders Outages Summary
| Output | FYTD | Planned | Forced | Time Hrs | Lost Sales | Total | Total | Feeder | Time | Date | Reason
Feeder | KWH | AVG KWH | Outages | Outages | Duration | Kwh | Outages | Time Hrs |  | min.
[9 empty] | Feeder #2A | 3 | 2021-02-03 | Faulty PLC by IPOS caused ESD activation that shutdown the vaporizer
Feeder #1A (13Kv) | 1075595.5 | 1211706.25 | 0 | 1 | 0.7 | 1121.5803 | 8 | 11.3667 | Feeder #3A | 3 | 2021-02-03 | Faulty PLC by IPOS caused ESD activation that shutdown the vaporizer
Feeder #2A (13 Kv) | 2331014.69 | 2791999.195 | 0 | 3 | 1.5333 | 5330.9474 | 32 | 32.9167 | Feeder #4A | 20 | 2021-02-03 | Faulty PLC by IPOS caused ESD activation that shutdown the vaporizer
Feeder #3A (13(Kv) | 858463 | 1024458.75 | 0 | 3 | 1.2667 | 1621.1904 | 19 | 15.4833 | Feeder #6A | 20 | 2021-02-03 | Faulty PLC by IPOS caused ESD activation that shutdown the vaporizer
Feeder #4A (13 Kv) | 1184914 | 1412961.0938 | 0 | 3 | 1.8667 | 3300.5961 | 17 | 17.5833 | Feeder #8B | 19 | 2021-02-03 | Faulty PLC by IPOS caused ESD activation that shutdown the vaporizer
Feeder #5A (13 Kv) | 2700000 | 3350000 | 0 | 1 | 0.7 | 2815.4327 | 4 | 4.6 | Feeder #9B | 19 | 2021-02-03 | Faulty PLC by IPOS caused ESD activation that shutdown the vaporizer
Feeder #6A (13 Kv) | 1668356 | 2007757.75 | 0 | 3 | 1.5667 | 3898.6095 | 10 | 15.85 | Feeder #10A | 3 | 2021-02-03 | Faulty PLC by IPOS caused ESD activation that shutdown the vaporizer
Feeder #9A (13 Kv) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Feeder #10B | 19 | 2021-02-03 | Faulty PLC by IPOS caused ESD activation that shutdown the vaporizer
Feeder #6B (24 Kv) | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6.0333 | Feeder #2A | 28 | 2021-02-03 | Unit 17 tripped on high exhaust temperature spread
Feeder #8B (24 Kv) | 3964477.125 | 5397222.1406 | 0 | 2 | 1.0167 | 6006.9327 | 6 | 6.0333 | Feeder #3A | 28 | 2021-02-03 | Unit 17 tripped on high exhaust temperature spread
Feeder #9B(24Kv) | 1667335.5 | 2207864.9868 | 0 | 2 | 1.35 | 3356.3005 | 8 | 12.25 | Feeder #4A | 29 | 2021-02-03 | Unit 17 tripped on high exhaust temperature spread
Feeder #10A(24Kv) | 1653656 | 1658502.1429 | 0 | 0 | 0 | 0 | 0 | 0 | Feeder #6A | 29 | 2021-02-03 | Unit 17 tripped on high exhaust temperature spread
Feeder #10B(24Kv) | 1221431.5 | 1431033.25 | 0 | 4 | 1.5833 | 2884.6735 | 32 | 21.8333 | Feeder #10A | 29 | 2021-02-03 | Unit 17 tripped on high exhaust temperature spread
TOTALS | 18325243.315 | 22493505.5591 | 0 | 22 | 11.5833 | 30336.2632 | 142 | 143.95 | Feeder #1A | 42 | 2021-02-06 | Unit 20 tripped causing island outage
[9 empty] | Feeder #2A | 61 | 2021-02-06 | Unit 20 tripped causing island outage
[9 empty] | Feeder #3A | 45 | 2021-02-06 | Unit 20 tripped causing island outage
[9 empty] | Feeder #4A | 63 | 2021-02-06 | Unit 20 tripped causing island outage
[9 empty] | Feeder #5A | 42 | 2021-02-06 | Unit 20 tripped causing island outage
[9 empty] | Feeder #6A | 45 | 2021-02-06 | Unit 20 tripped causing island outage
[9 empty] | Feeder #8B | 42 | 2021-02-06 | Unit 20 tripped causing island outage
[9 empty] | Feeder #9B | 62 | 2021-02-06 | Unit 20 tripped causing island outage
[9 empty] | Feeder #10A | 61 | 2021-02-06 | Unit 20 tripped causing island outage
[9 empty] | Feeder #10B | 63 | 2021-02-06 | Unit 20 tripped causing island outage
[9 empty] | Feeder #10A | 2 | 2021-02-18 | Feeder 10A tripped opem on underfrequency due to solar farm swing
0
0
0
0
0

## PR-Pag6
February - 2021
Power - Water Units Outages
|  | TOTAL NUMBER OF OUTAGES |  |  |  | PLANNED OUTAGES |  |  |  | FORCED OUTAGES
| This Month | FYTD | This Month | FYTD | This Month | FYTD | Duration | FYTD | This Month | FYTD | Duration | FYTD
Unit | Outages | Outages | Hours | Hours | Outages | Outages | Hours | Hours | Outages | Outages | Hours | Hours
Unit 10ST | 1 | 8 | 672 | 5832 | 1 | 8 | 672 | 5832 | 0 | 0 | 0 | 0
Unit 11ST | 1 | 8 | 672 | 5832 | 1 | 8 | 672 | 5832 | 0 | 0 | 0 | 0
Unit11BLR | 1 | 8 | 672 | 5832 | 1 | 8 | 672 | 5832 | 0 | 0 | 0 | 0
Unit 16 | 0 | 0 | 672 | 5832 | 0 | 0 | 672 | 5832 | 0 | 0 | 0 | 0
Unit 17 | 0 | 4 | 0 | 26.65 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 26.65
Unit 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Unit 20 | 1 | 8 | 0 | 4395.3167 | 1 | 8 | 0 | 4395.3167 | 0 | 0 | 0 | 0
Aggreko | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HRSG 21 | 1 | 8 | 672 | 5832 | 1 | 8 | 672 | 5832 | 0 | 0 | 0 | 0
HRSG 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTALS | 5 | 44 |  |  | 5 |  |  |  | 0 | 2
Plant Power Distribution
|  |  | This Month | FYTD | FYTD |  |  |  | Peak and Min. Load Data
|  |  | KWH | KWH | AVG. | [5 empty] | FYTD
Total 13KV Feeders |  |  | 9818343.19 | 94391064.31 | 11798883.0388 |  |  |  |  | This Month | AVG.
Total 24KV Feeders |  |  | 8506900.125 | 79482748.046 | 9935343.5058 |  |  | Peak Load (KW) |  | 35500 | 39091.25
Feeder Totals |  |  | 18325243.315 | 173873812.356 | 21734226.5445 |  |  | Day |  | Wednesday
Total Generation |  |  | 19883892.25 | 186915877 | 23364484.625 |  |  | Date |  | 2021-02-03
T1,T3,T4, T5, T6, T7 Available |  |  | 8291395 | 177632715 | 22204089.375 |  |  | Hour |  | 18:47
T1&T3&T4&T5&T6&T7 Losses* |  |  | 117165.435 | 1742816.272 | 217852.034
Net Distributed |  |  | 19766726.815 | 185173060.728 | 23146632.591 |  |  | Min. Load (KW) |  | 23290 | 25013.75
Line Department |  |  |  | 0 | 0 |  |  | Day |  | Sunday
Water Department |  |  |  | 0 | 0 |  |  | Date |  | 2021-02-07
Power Plant Services |  |  |  | 0 | 0 |  |  | Hour |  | 5:00
Administration & General |  |  |  | 0 | 0
Plant Station Service |  |  |  | 0 | 0
Net Available from Bus |  |  |  | 0 | 0
Wapa KWH From Dist |  |  |  | 0 | 0 |  | * meters under review
SwitchGear Bkr1 SS |  |  | 1079256.5 | 8790841 | 1098855.125
SwitchGear Bkr3 SS |  |  | 361867 | 2546076 | 318259.5
Total Station Service Power |  |  | 1378653.13 | 11359717 | 1419964.625
Net KWH Available for Sale |  |  | 18325423.315 | 173813343.728 | 21726667.966
Plant Unaccountable |  |  | 0 | 0 | 0
0
0
0
0
0

## PR-Pag7
February - 2021
|  |  | Fuel Allocation | BBLS
|  |  | Propane Fuel For Power | 72089.0952
|  |  | Propane Fuel For Water | 0
|  |  | No 2 Fuel For Power | 1607.2953
|  |  | No 2 Fuel For Water | 0
|  |  | O&M Factor for Water | 0
Power Boilers
11
TPBSFC
BLR11FUELCOST
0 |  | GT Fuel Allocation
HP Stm from WHB
GTFCAE
WHBHPSTMCOST
Combined Cycle |  | 0
WHB, 16. 17. 20
TGTFC |  |  |  |  | Electrc Power
GEN1617FUELCOST |  |  |  |  | Generation
1996028.5493 |  |  |  |  | TOTFUELCOSTPWR
|  |  | Gas Turbine |  | 3662267.9831
Power Allocation
Simple Cycle |  |  | GTFCA
GEN161720ADJFCOST
GEN 19 FUELCOST |  |  | 1996028.5493
63584.2339
RO Water
DIESEL |  |  |  |  | Production Cost
Emergency Gen.
DIESEL_EMER. |  |  |  |  | 208630.1026
0
Cost Calculated at:
| 69.2784 | per BBL for No. 2
| 52.1514 | per BBL for Propane

## PR-Pag8
February - 2021
Fuel Allocations
Fuel Summary |  |  |  | ITEM | Amount | FYTD
ITEM | Propane | No2 BBLS
|  |  |  | Electric Power Generation | 3662267.9831 | 28959097.1085
Inventory-Beginning of Month |  | 30080.1268 |  | Water Production* | 208630.1026 | 1417185.5451
Received During Month |  | 0 |  | Total #2 Fuel Cost | 111350.8443 | 3054402.7603
Consumed During Month |  | 1607.2953 |  | BBLS Propane for Power | 72089.0952 | 645489.3095
Inventory-End of Month |  | 28472.8314 |  | BBLS Propane for Water | 0 | 0
Calorific Value (BTU/GAL) | 91425 | 136999.0879 |  | BBLS No. 2 for Power | 1607.2953 | 43449.8514
|  |  |  | BBLS No.2 for Water | 0 | 0
|  |  |  | Propane BBL Cost | 52.1514
End of Month- Fuel in Tanks |  |  |  | No. 2 BBL Cost | 69.2784
|  | No 2 BBLS |  | * Note: Includes RO Electric Usage
|  |  |  | No. 2 Oil Used | This Month | FYTD
Tank 1 |  | 0 |  | No. 2 Units | BBLS No. 2 | BBLS No. 2
Tank 2 |  | 0
Tank 3 |  | 4425.75 |  | Unit 11 | 0 | 0
Tank 4 |  | 4114.71 |  | Unit 16 | 0 | 0
Tank 5 |  | 18987.72 |  | Unit 17 | 337.2299 | 11173.0543
Tank 6 |  | 944.64 |  | Unit 19 | 917.8075 | 30578.0679
Tank 7 |  |  |  | Unit 20 | 352.2579 | 1698.7293
TOTALS | 0 | 28472.8314 |  | Diesel Emergency | 0 | 0
|  |  |  | Total No. 2 Consumed | 1607.2953 | 43449.8514
Fuel Shipments |  |  |  | Propane Used | This Month | FYTD
|  | No2 | No2 | Propane Units | Gals | Gals
|  | Date | BBLS | Unit 16 | 0 | 0
|  |  |  | Unit 17 | 152377.8603 | 12051941.5695
|  |  |  | Unit 20 | 1416650.0361 | 2398132.8555
|  |  |  | Aggreko | 1458714.1036 | 12660476.575
|  |  |  | Total Propane Consumed | 3027742 | 27110551
TOTAL SHIPMENTS |  |  | 0
|  |  |  | Tank Fuel / Metered Fuel | Ratio
Used Oil recovered | 0 | Bbls
|  |  |  | No. 2 | 1.0492
|  |  |  | Propane | 0.95589
Ratio 0.95 to 1.05 acceptable
0
0
0
0
0

## PR-Pag9
February - 2021

## PR-Pag10
February - 2021

## PR-Pag11
February - 2021